­



­­­

**Access Control and Security Management Software**

**Architectural and Engineering Specifications**

TABLE OF CONTENTS

[PART I GENERAL 4](#_Toc8753751)

**[1.1](#_Toc8753752)****[GENERAL DESCRIPTION](#_Toc8753752)** [4](#_Toc8753752)

**[1.2](#_Toc8753753)****[SUBMITTALS](#_Toc8753753)** [4](#_Toc8753753)

[1.2.A Shop Drawings 4](#_Toc8753754)

[1.2.B Product Data 5](#_Toc8753755)

[1.2.C As-Built Drawings 5](#_Toc8753756)

[1.2.D Manuals 5](#_Toc8753757)

**[1.3](#_Toc8753758)****[QUALITY ASSURANCE](#_Toc8753758)** [6](#_Toc8753758)

[1.3.A Manufacturer Qualifications 7](#_Toc8753759)

[1.3.B Contractor/Integrator Qualifications 7](#_Toc8753760)

[1.3.C Testing Agencies 7](#_Toc8753761)

**[1.4](#_Toc8753762)****[WARRANTY](#_Toc8753762)** [8](#_Toc8753762)

[PART II PRODUCTS 9](#_Toc8753763)

**[2.1](#_Toc8753764)****[MANUFACTURERS](#_Toc8753764)** [9](#_Toc8753764)

**[2.2](#_Toc8753765)****[DESCRIPTION](#_Toc8753765)** [9](#_Toc8753765)

**[2.3](#_Toc8753766)****[PERFORMANCE - MONITORING](#_Toc8753766)** [10](#_Toc8753766)

[2.3.A Monitoring Mode 10](#_Toc8753767)

[2.3.B Graphics Screen 12](#_Toc8753768)

[2.3.C Communication Methods 13](#_Toc8753769)

**[2.4](#_Toc8753770)****[PERFORMANCE – PROGRAMMING & CONFIGURATION](#_Toc8753770)** [15](#_Toc8753770)

[2.4.A User Section 15](#_Toc8753771)

[2.4.B Video Section 19](#_Toc8753772)

[2.4.C Definition Section 21](#_Toc8753773)

[2.4.D Devices Section 25](#_Toc8753774)

[2.4.E Alarm Interface 28](#_Toc8753775)

[2.4.F Integrations 28](#_Toc8753776)

[2.4.G Virtual Alarm System 33](#_Toc8753777)

[2.4.H System Section 34](#_Toc8753778)

[2.4.K Options Section 38](#_Toc8753779)

[2.4.K Help Section 39](#_Toc8753780)

[2.4.L System Status Section 39](#_Toc8753781)

[2.4.M Various Tools 39](#_Toc8753782)

[2.4.N Video Vault 40](#_Toc8753783)

**[2.5](#_Toc8753784)****[PERFORMANCE – WEB/MOBILE APP](#_Toc8753784)** [40](#_Toc8753784)

[2.5.A EntraPass web 40](#_Toc8753785)

[2.5.B Mobile app - EntraPass go 51](#_Toc8753786)

**[2.6](#_Toc8753787)****[INTEGRATION](#_Toc8753787)** [54](#_Toc8753787)

[2.6.A SmartLink 54](#_Toc8753788)

[2.6.B Card Gateway 54](#_Toc8753789)

**[2.7](#_Toc8753790)****[REDUNDANCY & MIRRORING](#_Toc8753790)** [54](#_Toc8753790)

[2.7.A Redundancy Server 54](#_Toc8753791)

**[2.8](#_Toc8753792)****[SYBASE DATABASE ACCESS](#_Toc8753792)** [55](#_Toc8753792)

**[2.9](#_Toc8753793)****[HSPD-12 COMPLIANCE AND INTEGRATION](#_Toc8753793)** [55](#_Toc8753793)

**[2.10](#_Toc8753794)****[OPERATION](#_Toc8753794)** [56](#_Toc8753794)

**[2.11](#_Toc8753795)****[EQUIPMENT](#_Toc8753795)** [61](#_Toc8753795)

[2.11.Server, Database Access and Redundancy Server requirements 61](#_Toc8753796)

[2.11.B Global and Multi-Site Gateway, SmartLink and VideoVault, requirements 62](#_Toc8753797)

[2.11.C EntraPass Workstation requirements 62](#_Toc8753798)

[2.11.D Controllers 63](#_Toc8753799)

[2.11.E Kantech Telephone Entry System (KTES) 65](#_Toc8753800)

[2.11.F Network Communications Controller (KT-NCC) 65](#_Toc8753801)

[2.11.G Card and Reader Support 65](#_Toc8753802)

**[3.1](#_Toc8753803)****[TESTING](#_Toc8753803)** [67](#_Toc8753803)

**[3.2](#_Toc8753804)****[TRAINING](#_Toc8753804)** [67](#_Toc8753804)

**[3.3](#_Toc8753805)****[MAINTENANCE](#_Toc8753805)** [67](#_Toc8753805)

Redundancy Server**DATABASE ACCESS**Database AccessRedundancy ServerMulti-Site GatewayVideoVaultEntraPass Workstation

**PART I GENERAL**

* 1. **GENERAL DESCRIPTION**

The security management system (SMS) shall be a modular secure access management system used to better control employee and visitor movements at various establishments. The SMS shall maximize all tools offered by the Windows platform. All commands shall be accessible using nothing more than a mouse, and keyboard use shall be limited to documenting fields requiring numeric or alphanumeric data.

The operating program shall be multi-user, multi-tasking and capable of running on a non-proprietary CPU or virtual machines. The application software shall be based on a standard, high level programming language. The SMS shall be modular to facilitate its installation and the development of its capabilities while avoiding major modifications in its operation and in saving all defined system and historical data.

The server shall be a database server using a Sybase SQL embedded database. All database management tools shall be included, such as backup, indexing, and database cleaning tools. No third party database tools or licensing shall be required. The Global Gateways and Kantech Network Communications Controllers (KT-NCCs) control communications between the various door controllers and assume complete management of the site in case of a network communication interruption with the server. The Global Gateway or KT-NCC shall make all decisions. The Multi-Site Gateway shall communicate system information between the server and controllers. The EntraPass Workstations shall be the primary user interface to perform supervisory and programming functions.

The SMS shall enable the selection of at least two user languages. The basic dictionary shall include English, French, Spanish, Italian, Portuguese, Simplified Chinese, Dutch and German, however, the system shall include a vocabulary editor to be used in designing custom language dictionaries. The operator’s profile shall permit the integration of one of the two basic languages.

The SMS shall include RS-232/RS-485 communication link between the various system components as well as TCP/IP network interface capability. Field devices such as card readers, alarm inputs, control points, shall be connected to fully distributed intelligent field panels capable of operating without host computer intervention in a non-degraded mode.

The SMS shall be able to design customized ID cards directly from the access management software. No specific program or software other than the access management software and no additional licensing shall be required for this function. Any EntraPass Workstation shall be capable of being used as a badging station. Badging shall be fully integrated with the card database.

* 1. **SUBMITTALS**

1.2.A Shop Drawings

Prior to assembling or installing the SMS, the Contractor shall provide complete shop drawings, which include the following:

1. Architectural floor plans indicating all system device locations.
2. Full schematic wiring information for all devices. Wiring information shall include cable type, cable length, conductor routings, quantities, and point-to-point termination schedules.
3. Complete access control system one-line block diagram.
4. Statement of the system sequence of operation.
5. Riser diagrams showing interconnections.
6. Detail drawings showing installation and mounting.
7. Fabrication drawings for console arrangements and equipment layout.
8. Test and Commission site report

All drawings shall be fully dimensioned and prepared in DWG file format using AutoCAD.

1.2.B Product Data

Prior to assembling or installing the SMS, the contractor shall provide the following:

1. Complete product data and technical specification data sheets that includes manufacturer’s data for all material and equipment, including terminal devices, local processors, computer equipment, access cards, and any other equipment provided as part of the SMS.
2. A system description, including analysis and calculations used in sizing equipment required by the SMS. The description shall show how the equipment operates as a system to meet the performance requirements of the SMS. The following information shall be supplied as a minimum:

a. Central processor configuration and memory size

b. Description of site equipment and its configuration

c. Protocol description

d. Hard disk system size and configuration

e. Backup/archive system size and configuration

f. Startup operations

g. System expansion capability and method of implementation

h. System power requirements and UPS sizing

i. A description of the operating system and application software

1.2.C As-Built Drawings

At the conclusion of the project, the Contractor shall provide “as built” drawings. The “as built” drawings shall be a continuation of the Contractors shop drawings as modified, augmented, and reviewed during the installation, T&C and acceptance phases of the project. All drawings shall be fully dimensioned and prepared in DWG file format using AutoCAD.

1.2.D Manuals

At the conclusion of the project, the Contractor shall provide copies of the manuals as described herein. Each manual’s contents shall be identified on the cover. The manual shall include names, addresses, and telephone numbers of each security system integrator installing equipment and systems and the nearest service representatives for each item of equipment for each system. The manuals shall have a table of contents and labeled sections. The manuals shall include all modifications made during installation, checkout, and acceptance. Date of project commencement, milestones, CCO’s and completion to be included also. The manuals shall contain the following:

1. Functional Design Manual

The functional design manual shall identify the operational requirements for the system and explain the theory of operation, design philosophy, and specific functions. A description of hardware and software functions, interfaces, and requirements shall be included for all system operating modes. All operational changes required by customer are to be documented in writing where they differ from original specification.

1. Hardware Manual

 The hardware manual shall describe all equipment furnished including:

1. General description and specifications.
2. Installation and test and commission procedures.
3. Equipment layout and electrical schematics to the component level.
4. System layout drawings and schematics.
5. Alignment and calibration procedures.
6. Manufacturers repair parts list indicating sources of supply.
7. Load calculations of equipment operating at maximum load.
8. Software Manual

The software manual shall describe the functions of all software and shall include all other information necessary to enable proper loading, testing, and operation. The manual shall include:

1. Definition of terms and functions.
2. Use of system and applications software.
3. Initialization, startup, and shut down.
4. Alarm reports.
5. Reports generation.
6. Data base format and data entry requirements.
7. Directory of all disk files.
8. Operators Manual

The operator’s manual shall fully explain all procedures and instructions for the operation of the system including:

1. Computers and peripherals.
2. System startup and shut down procedures.
3. Use of system, command, and applications software.
4. Recovery and restart procedures.
5. Graphic alarm presentation.
6. Use of report generator and generation of reports.
7. Data entry.
8. Operator commands.
9. Alarm messages and reprinting formats.
10. System access requirements.
11. Maintenance Manual

The maintenance manual shall include descriptions of maintenance for all equipment including inspection, periodic preventive maintenance, fault diagnosis, and repair or replacement of defective components.

Maintenance manual shall also include a list of recommended spares, which are liable to be encountered as part of routine service procedures.

* 1. **QUALITY ASSURANCE**

1.3.A Manufacturer Qualifications

The manufacturers of all hardware and software components employed in the SMS shall be established vendors to the access control/security monitoring industry for no less than five years and shall have successfully implemented at least five systems of similar size and complexity.

1.3.B Contractor/Integrator Qualifications

1. The security system integrator shall have been regularly engaged in the installation and maintenance of integrated access control systems and have a proven track record with similar systems of the same size, scope, and complexity.
2. The security system integrator shall supply information attesting to the fact that their firm is an authorized Kantech global dealer.
3. The security system integrator shall supply information attesting to the fact that their installation and service technicians are competent factory trained and certified personnel capable of maintaining the system and providing reasonable service time.
4. The security system integrator shall provide a minimum of three (3) references whose systems are of similar complexity and have been installed and maintained by the security system integrator in the last five (5) years.
5. There shall be a local representative and factory authorized local service organization that shall carry a complete stock of parts and provide maintenance for these systems.

1.3.C Testing Agencies

1. The following hardware have been tested and listed by Underwriters Laboratories (UL) for UL 294 for access control system units.
2. KT-300
3. KT-400
4. KT-1
5. IP link
6. P225W26
7. P225KPW26
8. P225XSF
9. P225KPXSF
10. P325W26
11. P325KPW26
12. P325XSF
13. P325KPXSF
14. KT-MOD-REL8
15. KT-MOD-INP16
16. KT-MOD-OUT16
17. KT-3LED-Plate
18. KT-NCC
19. ioSmart readers
	1. KT-MUL-MT
	2. KT-MUL-SC
	3. KT-SG-MT
	4. KT-SG-SC
	5. KT-SG-MT-KP
	6. KT-MUL-MT-KP
20. The SMS shall be tested and listed by Underwriters Laboratories (UL) for UL 1076 for proprietary alarm units when using a KT-NCC Gateway and KT-400/KT-1 controller.
21. The hardware shall comply with the following regulatory requirements:
22. FCC Part 15 Class A.
23. FCC Part 15 Class B.
24. FCC Part 68 (TIA968).
25. ICES-003.
26. CE.
27. ECCN for AES 128 bit encryption for IP communication.
	1. IP Link, KT-400 or KT-1 only.
28. Government standards NISPOM 5-313 Automated Access Control Systems, DICD Annex F 2.3 Accept/Reject Threshold Criteria, JAFAN Annex D 2.3 Accept/Reject Threshold Criteria.
29. The ioSmart readers shall have an IP 55 rating.
30. The SMS shall support Americans with Disabilities Act (ADA) compliance in door and access operation.
	1. **WARRANTY**

The security management system (SMS) shall be provided with a 12-month product warranty from date of registration. Software version updates shall be available for no charge during this warranty. The software media warranty shall be 90 days.

**PART II PRODUCTS**

**2.1 MANUFACTURERS**

The security management system (SMS) shall be the Kantech EntraPass Global Edition.

**2.2 DESCRIPTION**

The security management system (SMS) shall be an integrated system that utilizes a Sybase SQL embedded database for the storage and manipulation of related data. The SMS shall include a server with applications software, Global Gateways or KT-NCCs for control of door controller communications, Multi-Site Gateways for communication between the server and controllers, operator and administrator EntraPass Workstations with appropriate software, hard copy printers and secure backup media. The security field devices (readers, door position switches, REX) shall communicate with the field panels via a dedicated cable network. The field panels shall communicate to the server via a Fast Ethernet 10/100, TCP/IP network, RS 232/RS 485 connection, or dial-up modem.

The SMS shall allow for growth and scalability from a smaller system to a larger, high-end, or enterprise system. The SMS shall be modular in nature, allowing system capacities to be easily expanded without requiring major changes to system operation. All defined system data as well as historical information shall be maintained. Customizable user interfaces shall allow the management of system information and activity for administrators and operators. The response time between the moment when a card is presented at the reader, and when the door is unlocked shall not exceed one second. The SMS shall include a badging solution with a GUI for badge design. No extra licensing shall be required for the badging solution.

The SMS shall be able to connect to an authenticated SSL/TLS or TLS cloud based or non-SSL/non-authenticated e-mail server for all e-mail features described. The SMS shall be able to connect to an SMTP or POP3 authenticated e-mail server.

 The SMS shall support the following devices:

128 EntraPass Workstations

200 Concurrent Web/mobile

128 Redundancy Servers

2 Redundant gateways per Multi-Site Gateway.

999 DVR/NVR recorders, options required. Forty is the default.

128 Global Gateways, KT-NCC

40 Multi-Site Gateways (or using dual gateway).

1,024 Door controllers per Global Gateway.

2,048 Connections per Multi-Site Gateway (max: 10,000 doors).

10, 000 Door controllers per Multi-Site Gateway.

10, 000 Readers per Multi-Site Gateway.

100, 000 Monitored points per Multi-Site Gateway.

100, 000 Control relays per Multi-Site Gateway.

128 Door controllers per KT-NCC (32 per local site – 8 TCP/IP per site).

1,024 Elevator controllers per Global Gateway.

4096 Card readers and/or keypads and/or elevator cabs of 64 floors each per Global Gateway.

69,632 Card readers and/or keypads and/or elevator cabs of 64 floors each per Multi-Site Gateway.

256 Card readers and/or keypads per KT-NCC (128 x 2) (512 if using KT-400).

100,000 Access cards per Global Gateway.

Unlimited Access cards

Unlimited Card families or site codes.

56,000 Cards per KT-NCC

262,144 Alarm points monitored by Global Gateway.

262,144 Control relays per Global Gateway.

2 Simultaneous user languages

**2.3 PERFORMANCE - MONITORING**

2.3.A Monitoring Mode

1. The SMS shall enable every operator to customize his/her desktop configuration. It shall be possible to modify the desktop appearance and to create up to eight desktops and to associate up to ten different display screens to each. It shall be possible to modify the size and position of all screens. It shall be possible to determine if these screens shall be floating anywhere on the desktop or fixed on the desktop. If the EntraPass Workstation is equipped with a dual output video card and two or more monitors, it shall be possible to distribute the screen to multiple monitors. However, each screen shall be able to be viewed alone or together depending on operator needs. Once these parameters are saved, the configuration shall automatically take effect whenever the operator logs in.

For all types of screens, it shall be possible to access the general properties of the screen by simply right clicking at the center of the screen. From there it shall allow for linkage between associated screens without having to exit the current screen or section. It shall be possible to right click events on the desktop for editing which shall bring the user directly to the card, door, or component window and back.

1. Message Screen

All events that occur shall appear in real time. The text shall include at least the date, time, and a pertinent description of the event as well as its condition. The display of this screen shall be customizable and a different background and message color can be used for every type of event.

In addition, the background color shall be chosen per operator. Events shall appear in their defined color or the operator shall have the option to choose a text color for the events.

All component modification events shall be tagged with addition (+), modification (=) or deletion (-) tag.

Every in-coming event shall be documented by one or more icons representing video images, photos, access card, server, gateway, controller, card reader, and relay or supervision point. It shall be possible to classify the events on the screen by sequence, date and time, type of event, or type of message. In addition, a text filter shall be available to facilitate searching. It shall be possible to access the most recent 100,000 transactions from this window without the need to request a special report.

It shall be possible to see the origin of the event so that the operator shall be able to see the event’s parent. For example, door and access events shall show the location (site) of the event.

It shall be possible to right click on an event and perform edit or other functions linked to the event.

1. Card Holder and Operator Photo Screen

When a card is presented to a card reader, the software shall automatically display the photograph of the cardholder in this window. From this screen it shall be possible to select the cardholder’s name, card number, event text, and comments as well as specify a door or group of doors for which the operator would like to display a photo. The SMS shall support the display of up to four pictures simultaneously. Furthermore the SMS shall allow that each picture box be assigned to a specific door for additional filtering. In addition the SMS shall support the ability to view the operator’s picture when operators generate events

1. Filtered Message Screen

This screen shall be a copy of the text messages screen except it shall be possible to select a specific message filter. The SMS shall include a choice of pre-configured filters and the ability to create customized filters. For every new filter it shall be possible to associate a name to it, select the type of event, select door, select EntraPass Workstation, select gateway, select supervision input, and select output.

1. Alarm Screen

Alarms that require an acknowledgement by an operator shall be displayed on this screen in text form only. The text shall include at least the date, time and description of the alarm, and its condition. It shall be possible to classify events on the screen by sequence, date and time, type of event, or type of message. A text filter shall be available in order to facilitate the search.

When the SMS pop-up is acknowledged by e-mail, the SMS shall display the operator’s name based on the e-mail that acknowledged it.

If instructions about an alarm are envisaged, they shall automatically appear in a second window on the screen. If a graphic is associated with the alarm, it shall appear automatically on the screen defined to this effect. The icon associated to the control point shall be represented and show the actual state of the point.

The operator shall be able to access a log book in order to document the alarm that occurred. Once this information is recorded in the log it shall not be erasable or modifiable. Operators shall also be able to see previous comments or system logs added this event.

Operators shall be able to run a report of the alarms from this window.

It shall be possible to associate video call-up with an alarm. When this occurs, the main screen shall become the video screen, not the alarm screen.

1. Video Screen (Video View)

 When the SMS is integrated with American Dynamics, INTEVO Advanced, INTEVO Compact, Exacq or Panasonic DVR/NVR, it shall be possible to view the video images of cameras associated with them. The SMS shall enable the creation of an unlimited number of video views, each one associated with up to 16 different cameras or graphics. It shall be possible for the operator to see at a minimum 48 cameras simultaneously using three video views per screen. It shall be possible for an operator to edit or modify an existing view or create a new one directly from this screen. For each video view it shall be possible to select sequential, mosaic pattern, or preset viewing modes.

 The SMS shall allow the operator to switch between pre-programmed video and a dynamic view. The Dynamic View shall allow the operator to select any camera and view it regardless without the need to create a new video view. The Dynamic view shall support up to 16 cameras at once.

 It shall be possible for an operator to access all the commands of a motion PTZ camera to include rotate on its axis, adjust its focus, and have a larger view of the image. Accessibility to camera images and commands shall be limited by operator security level.

No additional licensing shall be required to perform this function.

The SMS shall allow the operator to select video views based on site linking. Site linking allow SMS operators to navigate the SMS with ease by site or system wide.

1. Historical Message Screen

This screen shall allow operators to choose from a previously created custom report. Operators shall choose a start and end time, and a start and end date. The report will be populated in this window and have the same characteristics of the message screen including all right-click functions.

The historical message screen shall allow operators to add comments to any event to view and edit at a later stage.

2.3.B Graphics Screen

1. There are three options for graphics that appear as background on the screen. The first is a reproduction of the building(s) floor by floor. The graphic module shall be capable of importing files in BMP, EMF, WMF, JPEG, GIF, PCX, PNG, TIF, or PCD formats.
2. The second option is using web pages, or WebViews, as background on the screen. This can be used in the following manners:
	1. Accessing to DVR web servers.
	2. Embedding default web pages into operator desktops.
	3. Adding an IP camera onto a video view.
	4. Embedding intranet pages or directories into the operator environment.
	5. Adding PDF, Word documents, to the desktop.
	6. Accessing to network cameras from the Web.
	7. HTML or PDF pop-up instruction on alarm.
	8. Integrating report folders in the desktop for quick access.
3. The third option is to assign a live video view as background on the screen if video integration is being utilized.
4. For all three options, control points shall be represented by a descriptive icon. Control points include EntraPass Workstations, gateways, controllers, card readers, doors equipped with either card readers or supervision contacts, cameras, relays, cameras, video views, task triggers and input monitoring points such as motion sensors. The icons shall be animated, meaning they shall represent the state of the point to which they are associated in real time. Every graphic shall support at least 100 control points.
5. A right-click on an icon shall directly access the manual commands of each control point. A door shall be capable of but not limited to: temporarily unlocking, manually unlocking or locking, enabling or disabling a reader, viewing the reader’s comments, and enabling or disabling the KT-400 or KT-1 door contact. A supervision point shall be capable of being enabled or disabled. A control relay shall be capable of being activated, deactivated, or temporarily activated. Cameras shall be capable of viewing images or live video.
6. No additional licensing shall be required to perform this function.
7. The SMS shall allow the operator to select graphics based on site linking. The SMS operators use site linking to navigate the SMS with ease by site or system wide.
8. This screen shall allow operators to bring up three previously created areas.
9. The cardholder shall be displayed in real time as they enter or exit the areas. The SMS automatically refreshes the list.
10. The operator shall have the ability to right-click an area to; empty the area, find a specific cardholder, and move cardholders to another area.
11. The area screen shall be configurable to include a user definable item from the cardholder list. The user shall choose from the following user defined items: event date and time, entry or exit reader, the last reader swiped and the time is was swiped.

2.3.C Communication Methods

1. The SMS shall ensure the communication to remote sites over a LAN or WAN/Internet using a dedicated communication server device, Kantech IP Link, KT-1 controller or the KT-400 controller. This shall only be applicable with the use of Multi-Site Gateways. It shall use 128-bit AES encryption for communications. It shall reduce bandwidth consumption by managing the communication protocol of Kantech controllers at the remote site. Polling of Kantech controllers shall be done by the Kantech IP Link, KT-1 controller or KT-400 in the field and not over the network. The Kantech IP Link, KT-1 controller or KT-400 shall provide support for up to 32 door controllers. The Kantech IP Link, KT-1 controller or KT-400 shall be configured from the access software or from a web page which has the security feature of being disabled after successful use.
2. For connections that do not have network links, communication to remote connections shall be ensured by dial-up modems. This shall only be applicable with the use of Multi-Site Gateways. The SMS shall support up to 32 such modems that can simultaneously transmit or receive data from remote connections. No modem shall be dedicated to a specific connection; communication shall be established where the first connection calling shall have access to the first available modem, and so on.
3. Each Multi-Site Gateway should be able to control 32 local controller connections by using the RS-232/RS-485 protocols via serial or USB port. In addition, each Multi-Site Gateway should be able to control up to 2048 (10,000 doors maximum Ethernet connections using TCP or UDP protocols, via the use of the Kantech IP Link, KT-1 or KT-400, of 32 controllers each.
4. The SMS shall offer the ability for each Multi-Site Gateway to have up to 2 redundant gateways. The redundant gateways shall be monitored and active with the SMS. In the case of primary gateway failure the redundant gateway shall automatically take control and controllers shall start communicating with this gateway.
	1. A reload of the controllers shall not be acceptable or needed
	2. The SMS shall update the primary and redundant gateways at the same time. They shall at all times have the latest values.
	3. The SMS shall instantaneously make the redundant gateway active without any human intervention in case of failure on the primary gateway.
	4. The SMS shall allow operators to proactively swap to the redundant gateway in case of planned maintenance.
	5. The customer IT shall configure their network to allow incoming connections to be active on both primary and redundant gateways.
	6. The SMS shall unlock each redundant gateway with a license.
5. The SMS shall differentiate between sites and connections. A connection shall be a hardware connection of controller over IP, direct, or dial up to the Multi-Site Gateway. A site shall be a collection of any connection from any Multi-Site Gateway.
	1. Operators shall be able to add connections to sites as needed.
	2. Operators shall assign access levels to card holders via the site. Having to assign an access level to every connection shall be unacceptable as this is time consuming.
	3. Operators shall be able to view, lock, and unlock all doors belonging to a site regardless of their connection.
		1. Operators shall have the option to expand the site and see where which connection the doors belong to
	4. When programming access levels operators shall see all the doors belonging to one site. From there the operator shall be able to assign a schedule to a door for the user’s access.
	5. Operators shall be able to take existing connections that are not part of any site and merge them into existing sites.
		1. The SMS shall give the option to merge identical schedules in order to remove duplication and unwanted schedules.
		2. The SMS shall give the option to enter a duplicate name as a prefix.
		3. The SMS shall give the ability to rename the connection’s access levels names
		4. The ability to reprogram access levels, and other items shall not be available.
6. Each site and connection shall have the ability to have 20 user definable fields. The field label names shall be changeable.
	1. Operators shall be able to enter up to 40 characters per field.
7. Each Global Gateway should be able to support up to 32 loops using the RS-232/RS-485 protocols or via Ethernet with a KT-400, KT-1 AES 128-bit AES encryption or the Lantronix® UDS1100. Each local loop can support up to 32 controllers and each Ethernet loop can support up to 8 controllers.
8. Each KT-NCC should be able to support seven loops. The loops shall be field configurable using the SMS as either of the following options:
	1. The KT-NCC shall support three direct loops using the RS-232/RS-485 protocols. The KT-NCC should also be able to support up to four Ethernet loops with a KT-400, KT-1 AES 128-bit AES encryption, or the Lantronix® UDS1100. Each direct loop can support up to 32 controllers, and each Ethernet loop can support up to eight controllers.
	2. The KT-NCC shall support seven Ethernet loops with a KT-400, KT-1 AES 128-bit AES encryption, or the Lantronix® UDS1100. Each Ethernet loop can support up to eight controllers.
9. The SMS shall ensure the communication to remote KT-NCCs over a LAN or WAN using TCP/IP. The KT-NCC shall only communicate with the Global Edition of the SMS using a proprietary Kantech communication protocol. The SMS shall provide the option to enable or disable encryption for each KT-NCC individually. The SMS shall allow the custom configuration of the TCP port for each KT-NCC. The SMS shall support up to 128 KT-NCCs.
10. In all communication methods, the door controller shall retain in their memory all necessary data for controlling doors that they supervise. In case of communication failure, the door controller shall execute all its functions normally.
11. When using a KT-1 it shall be possible to use the auto-enrollment functionality. An operator shall be able to press a button on the KT-1 controller, which shall find the EntraPass Multi-Site Gateway, gobal gateway or KT-NCC. Once found by the SMS, the operator shall quickly and efficiently be able to enroll the KT-1.
	1. The auto-enrolment shall work on a local LAN segment of the network
	2. The SMS shall display in dedicated list all unassigned KT-1. From the EntraPass EntraPass Workstation or Web. The operator shall simply pick the KT-1 they are interested in.
	3. The SMS shall allow the following functionality using the auto-enrolment wizard:
		1. Assign a KT-1 to a site/connection.
		2. Name the door
		3. Activate the exit reader.
		4. Activate the door contact.
		5. Activate the Request to exit.
	4. The SMS shall auto-fill the MAC address and serial number. Having to manually enter the MAC address or serial number in the auto-enrolment shall not be acceptable.

**2.4 PERFORMANCE – PROGRAMMING & CONFIGURATION**

2.4.A User Section

1. This section shall include all functions involved in the issuance of an access or ID card as well as database search and importation tools. During the addition or modification of a card, information about the card shall be sent to the door controllers affected by these new parameters as soon as the operator accepts the addition or modification. An additional command requiring a reloading of the cards database in the door controllers shall not be acceptable.
2. The SMS shall enable the creation and definition of a user access card. There can be up to five cards per user and users can be managed by cardholder name or card number. When creating user cards, the operator shall be able to select a card format directly from a card dialog and enter the card number as it is printed on the card.
3. The SMS shall allow adding door access exceptions to the cardholder’s list of access rights.
	1. The SMS operator shall be able to provide a pre-defined access level and separately add a specific door to be part of the cardholder’s access right.
	2. The door shall have its own schedule
	3. The SMS operator shall have to option of allowing or disallowing access to that door based on that schedule
	4. There shall be no limit of the amount of doors that can have exceptions.
	5. The KT-400 and KT-1 shall keep in memory the door access exceptions even in standalone mode. This feature shall be available with the KT-400 and KT-1.
	6. The KT-100, KT-300, KT-200 shall support the door access exceptions while communicating with the KT-NCC or Global Window Gateway. The controllers shall always work with their access levels while in standalone mode.
4. The following user information shall be able to be saved in the user section:
	1. Five card numbers each with their own expiration date, trace and lost or stolen statuses.
	2. Each card number shall have their own expiration date and expiration hour.
	3. The card numbers shall have the option to be mandatory or not.
	4. First and last name.
	5. Card type.
	6. Additional information (40 fields).
	7. Start date.
	8. Expiry date.
	9. Personal ID number (PIN).
	10. State of the card.
	11. Multi-swipe activation.
	12. Comments.
	13. User’ e-mail address
	14. go Pass configuration
		* 1. Notification
			2. Language

HID mobile credentials management.

In addition, it shall be possible to associate a photograph, signature, and badge template to a card. The picture of the card holder shall always be visible when the profile is active on the screen.

4. The SMS shall allow for the creation of an unlimited number of card templates to be used as ID cards. Template parameters include name, number of sides, and size. It shall be possible to directly print a template on an access card. The operator shall be able to design customized badging templates directly from the access management software. No specific badging program or software other than the latter and no additional licensing shall be required for this function. Any EntraPass Workstation shall be capable of creating ID cards based on operator security level. The following items shall be capable of being added to and modified on a badge template:

* 1. All information fields associated to a cardholder.
	2. Bar code
	3. Text zone
	4. Start date, expiry date, today’s date.
	5. Saved images and logos.
	6. Borders
	7. Rectangles (including rounded rectangles, ellipse).
	8. Lines and arrows
	9. Photograph (can be cropped).
	10. A background.
		1. The SMS shall offer the possibility of modifying the parameters of a group of cards simultaneously based on card type. The system shall enable the creation of an unlimited number of card types. The following fields shall be modifiable:
			1. Card status (valid, invalid, lost, stolen).
			2. Card monitored (yes, no).
			3. Start date (schedule)
			4. End date (schedule)
			5. Delete after expiration (yes, no).
			6. Wait on keypad (yes, no).
			7. Access group (selection menu).
			8. Template model (selection menu).
		2. The operator shall be able to search for a card by last or first name, card creation date, card number, or any of the ten fields of user definable information.
		3. The system shall display the last card transactions, namely the latest sixteen denied access events, authorized events, database events, and/or time & attendance events.
		4. The SMS shall offer an extended last card transactions window; to get a complete access events report the SMS operators shall simply enter the start date and time, and the end date and time.
		5. The operator shall be able to quickly search by username directly on the card window. The SMS shall automatically provide the 24 first search results by simply typing the value and then expanding the dropdown list.
		6. The operator shall be able to view quickly the cardholder’s door list.
			1. Operators shall be able to export the door access list.
			2. A detailed view of the door’s schedule shall be shown when selecting a door.
		7. The operator shall have the option of expanding the comments field in the user section for better viewing.
		8. When using a Global Gateway or KT-NCC, the cardholder’s five cards shall be managed as one for time and attendance, anti-passback, sector/area control purposes. Card holders shall be able to use any of their five cards without violating the door security policies.
		9. The SMS shall enable the creation of an unlimited number of Import/Export models, give them a name, select required fields, select their layout, and determine the filed delimiter. This shall allow for acceleration of the data entry process by importing databases from a spreadsheet.
			1. The SMS shall allow the operator to import and export cards using a unique card identifier. If required, the unique identifier can replace the card number for importing and exporting card numbers.
		10. The SMS shall allow for 250 access levels programmed per Global Gateway or KT-NCC. Every card shall be assigned an access level, which shall determine where and when the access card will be valid. When the system consists of several sites or gateways, it shall be possible to use batch programming of access levels. If using a Multi-Site Gateway the system shall support 250 access levels per site on Multi-Site Gateways.
1. The SMS shall allow operators to quickly add a door to a list of access levels.

The SMS operator shall select a door and see a list of access levels.

The SMS shall return to the access level assigned to the door shown on the schedule. If the door is not assigned to an access level, it shall show None.

The SMS operator shall be able to change any of the doors assigned access levels by simply changing the schedule.

* + 1. The SMS shall support up to a total of 13 access levels for each card user per Global Gateway or KT-NCC. Each access level can have its own expiry date.
		2. The SMS shall support a total of five access levels for each card user per site/connection when using the Multi-Site Gateway. This feature shall be available with the KT-400 and KT-1. The SMS shall advise the operator if doors are not supported when adding additional access levels (two to five).
		3. The SMS shall support the export of all cards linked to an access level in the Sybase database, the export shall use an Adobe PDF or a CSV format, or print.
		4. The SMS shall support the export of the access levels programmed in the Sybase database, the export shall use an Adobe PDF or a CSV format, or print.
		5. The SMS shall allow for creation of tenant lists that can be imported in the Kantech Telephone Entry System (KTES) units. The lists shall be easy to complete and allow for up to 3,000 tenants in each list. The SMS shall support the creation of unlimited amounts of tenant lists.
		6. The SMS shall allow importing and exporting of tenant lists. The operator shall have the ability to choose which fields to import and export.
		7. The following tenant information shall be able to be saved for each tenant:
			1. Tenant name
			2. Tenant ID (customizable in length per tenant list).
			3. Primary telephone number
			4. Secondary telephone number
			5. Tenant PIN (customizable in length per tenant list).
			6. Pin access schedule
			7. Tenant level
			8. Tenant language
			9. Card number
			10. Disable card trace
			11. Start/end date
			12. No disturb schedule
			13. Prioritized tenant in the display list.
			14. Call second phone number, option schedule.
			15. Ability to call the second phone number only (does not call primary) during valid schedule.
		8. The SMS shall allow for a card number to be assigned to a specific tenant. The KTES unit will be able to send the card number to other controllers of a Wiegand protocol.
		9. The SMS shall allow for an unlimited amount of card types. Cards types shall be used to group cards together for ease of management. Card types shall have the option of being assigned a card access group template. Card access groups shall be copied to the card holder’s profile to give the card holder access levels.
		10. The SMS shall provide the possibility to perform card batch operations. The batch card modifications shall take effect in real time. Each batch operation shall allow for a batch of cards to be changed based on their card type. The batch card modification shall be able to change the following:
			1. Card state
			2. Supervisor level
			3. Card count value.
			4. Card tracing
			5. Start date
			6. End date
		11. With deletion on expiration.
			1. Waiting for keypad
			2. Card access group
1. Replacing access levels
2. Updating access levels
3. Adding new access levels.
4. Updating and adding new access levels.
	* + 1. Card badge layout

2.4.B Video Section

1. The SMS shall be capable of being combined with up to 128 American Dynamics Intellex digital video recorders, American Dynamics Hybrid DVR (HDVR), American Dynamics TVR2, American Dynamics VideoEdge, American Dynamics VideoEdge Hybrid NVR v4.03, INTEVO Advanced, INTEVO Compact, and Exacq A, Z, ELS, ELXS, ELX-IP, ELX-SR, LC, LC-IP series DVR/NVR without any additional licensing.
	1. The SMS shall allow the operator link video servers and cameras to a site. Site linking allow SMS operators to navigate the SMS with ease by site or system wide.
2. From any of the EntraPass Workstations it shall be possible to do the following:
3. View one or more camera images from different sources.
4. Query the history of each recorder and view images saved on disk.
5. View, modify, or delete programming parameters of a recorder.
6. Control the movement of all motion cameras directly with the EntraPass Workstation mouse of the SMS (PTZ control).
7. Export camera images to hard disk and video vault (capable of exporting multiple formats, password protected to protect chain of evidence).
8. The SMS shall ensure the time management and synchronization for all the American Dynamics DVR/NVR. It shall be possible to determine the time refresh frequency on the network for the American Dynamics DVR/NVR. The SMS shall allow for configuration of each DVR/NVR. For each recorder it shall be possible to:
	1. Assign a name.
	2. Determine the recorder type.
	3. Determine the network IP address or domain name.
	4. Alternative IP address or domain name.
	5. Manually configure the video, communication and event ports.
	6. Determine the number of cameras.
	7. Determine the query frequency.
	8. Determine the number of failed queries required before a loss of communication message is displayed on the screen.
	9. Import camera details from existing video servers.
9. The SMS shall define the programming parameters for every camera connected to a DVR/NVR. For each camera it shall be possible to:
	1. Assign a name.
	2. Determine the type of camera.
	3. Assign a representative icon for identification on a graphic screen.
	4. Determine if the camera image can be visible on a video view.
	5. Determine the type of recording.
	6. Determine which events from the recorder should display an alarm message on the screen.
	7. Determine the number of pre-selections desired.
	8. Determine the number of patterns desired.
	9. Add comments to record in the video vault.
10. The SMS shall allow for the creation of an unlimited number of video views. For each video view it shall be possible to connect up to 16 cameras from various sources.
11. The SMS shall be able to incorporate the same view on multiple cameras from different American Dynamics Intellex DVRs or graphics. Furthermore, on different video views the SMS shall be able to incorporate multiple camera sources from different American Dynamics HDVRs, INTEVO Advanced, INTEVO Compact, Exacq or graphics. In addition, on different video views the SMS shall be able to incorporate multiple cameras source from different American Dynamics TVR2 or graphics. In addition, on different video views the SMS shall be able to incorporate multiple camera sources from different American Dynamics Video Edge NVRs or graphics. Also, on different video views the SMS shall be able to incorporate multiple camera sources from different Panasonic DVR/NVR of the same model or graphics.
12. The video view programming parameters make it possible to complete the following:
	1. Assign a name
	2. Determine the view size.
	3. Determine the refresh rate of the image.
	4. Determine whether to show metrics.
	5. Determine whether to show camera controls.
	6. Determine whether to show overlays.
	7. Determine whether to auto-hide text.
	8. Determine whether to activate image zoom.
	9. Determine whether to activate video sequence.
	10. Determine delay before sequence launch.
	11. Determine camera display delay.
	12. Determine display pre-selection delay.
	13. Determine pattern display delay.
	14. Determine graphic display delay.
	15. Determine display mode (1x1, 2x2, 3x3, and 4x4).
	16. Incorporate up to 16 cameras from various sources or 16 graphics.
13. The SMS shall be able to trigger, from one or more events (specific), the start of a recording on a recorder with one or more cameras connected to it. The SMS shall allow for the creation of an unlimited number of video triggers. The SMS shall allow for the creation of an unlimited number of recording parameters. For each recording parameter it shall be possible to:
14. Define a name
15. Select the DVR/NVR to which this recording parameter refers.
16. Select the camera to which this recording parameter refers.
17. Associate a pre-selection or size.
18. Determine the start-recording trigger.
19. Determine the pre-alarm time.
20. Determine the total recording time.
21. Determine the stop recording trigger.
22. It shall be possible for a video event on one DVR/NVR to trigger an action on another DVR/NVR.
23. The SMS shall allow the playback of all recordings stored on the hard drive of any of the DVR/NVR. The operator shall be able to save the video into the video vault.
24. The SMS shall provide the operator access to the complete list of normal and abnormal events that required the activation of video recording. The sequence of images can be saved to a hard drive for subsequent consultation and shall be encrypted. The SMS shall allow the operator to access a complete list of alarm recordings in progress including origin of the alarm. The SMS shall be capable of displaying a list of exported videos.
25. It shall be possible to view recorded video tagged to an access or video event by quick linking from the message desktop.
26. The SMS shall be capable of connecting by default 128 American Dynamics, INTEVO Advanced, INTEVO Compact, Exacq or Exacq DVR/NVR with no additional options needed.
27. The SMS shall allow increasing the number of American Dynamic DVR/NVR, INTEVO Advanced, INTEVO Compact, Exacq or Exacq in groups of 128 by the use of option codes. The SMS shall support unlimited connections.
28. The SMS shall allow for installation of remote modular video managers. The remote video managers shall be available only after the first 128 connections have been reached.

2.4.C Definition Section

1. The SMS shall allow the creation of 100 schedules per Global Gateway or KT-NCC and 100 schedules per Multi-Site Gateway and an unlimited number of system schedules. A schedule can be associated with a supervision point, a relay, an access level, a door, elevator floor, an operator, or an event. The SMS shall allow time zone management.
2. With a Global Gateway or KT-NCC, each schedule shall include up to 20 intervals. The 20 intervals shall be available for all controllers (including legacy controllers). The KT-400 or KT-1 shall keep all 20 intervals in memory when in standalone mode.
3. With a Multi-Site Gateway, specific schedules, which include up to 20 intervals, shall be available for the KT-400 or KT-1. The KT-400 and KT-1 shall keep all 20 intervals in memory when in standalone mode. By default each schedule shall support four internals
4. The SMS shall allow the creation of 366 holidays. It shall be possible to define a name, define a date, and determine the type. The SMS shall allow the operator to view all the holidays defined in holiday type and sites by viewing them all in a yearly calendar.
	1. The SMS shall not require that to create the same date multiple times when affecting certain sites. The SMS shall allow that the same holiday date can be used on some sites or all the entire system,
5. The SMS shall allow the creation of up to 100 areas per Global Gateway or KT-NCC. Areas shall be the basis for using input/output synchronization (anti-passback), global anti-passback and use of time and attendance. They shall define how to control circulation within an area of controlled doors. Area features shall include supervisor level control, mustering, occupancy limit, and timed anti-passback.
6. The SMS graphics shall enable operators to view the exact location of a component installed at the site, or the state of components and peripherals represented in the graphic such as doors, contacts, motion sensors, controllers, video views and cameras. The SMS shall allow for the creation of an unlimited number of graphics. The components on the graphics represented by icons as well as the graphics themselves shall have the ability to be modified. The SMS shall allow for printing of the graphics with their respective components on the graphical floor plan.
	1. The SMS shall allow the operator link graphics to a site. Site linking allow SMS operators to navigate the SMS with ease by site or system wide.
7. The SMS shall allow the management of 2,048 elevator cabs of 64 floors each for each gateway. It shall be possible to associate a schedule to the call button. Outside of the schedule, a valid card for a particular floor will have to be presented to the cab reader for it to be activated. The floor selection button group associated with the card’s access level will become operational for a predefined duration and all other buttons shall become inactive. The SMS shall allow the creation of groups of floors and access levels.
8. With the Multi-Site Gateway, the KT-400 controllers, each elevator floor shall have the ability to associate to its own unlock schedule. Thus, every elevator floor shall be available without a card read at its respective time.
9. The SMS shall provide the possibility of setting up guard tours with existing components of the system. Card readers, magnetic contacts and motion sensors can be used as control stations for the guard tour. Key switches can also be located at strategic points for the guard to activate.
10. The SMS shall provide the possibility to setup unlimited tasks using the task builder. The operator shall be able to create e-mail templates for a multi-site environment with a variable to populate the e-mails dynamically. Using the command GUI menu, the operator can program commands for any component in the SMS. Commands such as but not limited to lock, unlock, temporary unlock, toggle, back to schedule for the doors, relays, inputs and enable and disable readers. The operator can also program commands for specific card count. The commands should be able to accept specific components or variables that can filled dynamically.
11. The SMS shall provide the possibility to setup unlimited batch card operations using the task builder. The batch card modifications shall take effect in real time. Each batch card modifications task shall allow for batch cards to be changed based on their card type. The batch card modification task shall be able to change:
12. Card state
13. Supervisor level
14. Card count value.
15. Card tracing
16. Start date
17. End date
	* 1. With deletion on expiration.
18. Waiting for keypad.
19. Card access group.
20. Replacing access levels.
21. Updating access levels.
22. Adding new access levels.
23. Updating and adding new access levels.
24. Card badge layout.
25. The SMS shall provide the possibility to assign previously created tasks to be triggered on specific components and specific events.
26. The SmartLink task commander shall process the command from the first available SmartLink application on the SMS.
	1. The use of a specific SmartLink to run the SmartLink task commander shall not be accepted. The SMS shall accept many SmartLinks to be installed thus providing a redundant SmartLink for all SmartLink task commander tasks.
27. It shall be possible to associate a relay or group of relays to an event from any controller using a Global Gateway or KT-NCC. These event parameters allow activating, de-activating or temporarily activating individual or groups of relays from any controller within a Global Gateway or KT-NCC based off any IO or other controller generated event within the gateway.
28. The SMS shall allow for the creation of unlimited instructions. These instructions shall be attributed to one or more events that will be used in documenting the event and guide the operator on duty in performing tasks. It shall be possible to edit the instructions in two different languages
29. The SMS event trigger shall also serve the alarm acknowledgement (pop-ups) configuration. Pop-ups shall be configured to alert SMS operators in real time of specific events on specific components.
30. The SMS shall allow how pop-ups occur by allowing the SMS operator to configure how a component (or components) and specific event (or events) are sent to the SMS EntraPass Workstations and/or e-mail.
	1. For each pop up, the SMS operator shall be able to choose the following but will not be limited to them:
		1. Event (or events)
		2. Component (or components)
		3. EntraPass Workstation (or EntraPass Workstations) receptions.
		4. Instructions
		5. Schedule the pop-ups occurs.
		6. Instructions
		7. Mandatory operator comments
		8. E-mail notification
		9. Able to acknowledge by e-mail
31. When the alarm pop-up occurs in real time, the SMS pop-up shall display the following but will not be limited to them:
	1. Date/time
	2. Event
	3. Component name
	4. Instructions
	5. Video playback of associated camera and video clip created.
	6. Automatically opens live video of associated camera.
	7. Able to acknowledge or temporary suspend an alarm.
	8. Audible sound playing wave file to audibly alert SMS operator.
32. When the alarm pop-up occurs in real time, if configured correctly, the SMS pop-up will send an e-mail with the following items but will not be limited to the following:
	1. Date/time
	2. Event
	3. Component name
	4. Instructions
	5. Event assigned color
	6. Able to acknowledge alarm
33. The SMS shall support up to 999 action schedulers. These action schedulers shall allow the user to perform actions on the SMS controllers on a pre-defined timeframe.
	* + - 1. Each action scheduler shall allow up to eight different components to be triggered. These components can be from the same controller or a different controller.

With the SMS Multi-Site Gateway, the action scheduler shall be stored in the KT-400 and KT-1. Once programmed by the SMS, the controller shall not need the SMS to trigger the action scheduled.

With the SMS global windows gateway or KT-NCC connected, the action scheduler shall be stored the on the SMS global windows gateway or KT-NCC making the action scheduler available for all SMS controllers.

* + - * 1. The action scheduler shall allow but will not be limited to the following:

Toggle door unlock

Unlock door

Relock door

Temporarily unlock door

Activate relay

Deactivate relay

Temporarily activate relay

Arm door partition

* + - * 1. The action scheduler shall be scheduled to trigger at limited intervals but will not be limited to these intervals:

Once on a specific date and time.

Daily at a specific time until a specific date.

Weekly at a specific time until a specific date.

* + - * 1. The SMS shall also allow the SMS to trigger a task (task builder) within the action scheduler.

These tasks shall be SMS dependent but can trigger anything configurable in the SMS tasks.

* + - * 1. The SMS shall offer overview windows were SMS operators can easily see the upcoming action schedulers.

The SMS operator shall be able to see the upcoming action schedulers in a the following views:

Daily

Weekly

Monthly

Yearly

“Bring me to the next action” button shall bring the SMS operator to the next action scheduled

The SMS operator shall be able to see if the action scheduler is a one-time action or a reoccurring action without having to open the action scheduler.

* + - * 1. The SMS operator shall be able to add keywords in the action scheduler during programming. This will allow the SMS operator to quickly search for the actions using the action scheduler name or keywords programmed.
				2. The SMS shall give the option to delete the action scheduler once it is completed.

2.4.D Devices Section

1. The physical components of the SMS including EntraPass Workstations, Multi-Site Gateways, gateway, site, controllers, KTES, doors, relays, ioSmart readers, ioSmart reader templates and monitored inputs shall be individually configured and defined. Individual sites shall also be defined. The software shall allow the use of a controller express setup feature in order to minimize the time needed for controller definition.
2. Each component in the devices section shall allow for a comment section per component. The SMS shall allow for an unlimited amount of characters in the comment section.
3. The SMS shall allow to migrate from the SMS legacy controllers to KT-400 and KT-1 without having to reprogram the controllers, access levels, doors and their respective associations.
	1. The SMS controller in the database shall only take a second.
	2. The SMS shall not in the background erase or reprogram the controller. By migrating and not erasing or reprogramming, the SMS will allow any custom integration and SMS associations to continue to work, as the controllers are the same.
	3. The SMS shall allow to migrate from a KT-100, KT-200, KT-300, KT-1 to a KT-400.
	4. The SMS shall allow to migrate from a KT-100 to a KT-1.
	5. The SMS expansion modules shall be reprogrammed manually.
	6. The following values at the minimum shall remain the same after the migration:
		1. Reader and keypad types.
		2. Anti-passback settings.
		3. Input end of line (EOL) resistor settings.
		4. Door name
		5. Unlock times
		6. Door unlock schedules.
		7. Door contact settings.
		8. REX contact settings.
		9. Intrusion integration settings.
		10. Access level programming.
		11. Reporting filters
		12. Workspace division settings.
4. The SMS shall support the programming of the ioSmart readers and ioModules with the KT-400 and KT-1 controllers over 128-bit AES encrypted RS-485 communication.
	1. The SMS shall offer a reader template where the SMS operators can customize the ioSmart behavior of the following items but not limited to:
		1. HID Prox 125 khz support
		2. ioSmart native support
		3. Mifare Plus, Mifare classic card serial number support.
		4. ISO 14443b card serial number support
		5. BLE Active /Inactive
		6. Keypad illumination intensity
			1. Keypad always on
			2. Keypad dim
			3. Keypad off but wake up on touch.
		7. LED Color management for the following but not limited:
			1. Tamper in alarm
			2. Standby
			3. Key press
			4. Communication failure alarm
			5. Low power
			6. Lock power trouble
			7. Access result, can have different LED patterns of the same color for the following results, but is not limited to:
				1. Access granted
				2. Access denied—Bad access level
				3. Access denied—Card expired
				4. Access denied—Lost or stolen
				5. Access denied—Card unknown
				6. Door armed/disarmed
				7. Wait for keypad
				8. Valid floor selection (when doing elevators)
				9. Invalid floor selection (when doing elevators)
				10. Request to exit
				11. Time out on request to exit
				12. Time out on access granted
				13. Door open to long
				14. Pre-alarm door open too long
				15. Wait for second card
				16. Multi-swipe denied
	2. The SMS shall offer a default reader template and allow for custom reader templates to be created by the SMS operators.
	3. The Reader templates shall be configured once and be available for all controllers.
		1. Changing the reader template shall automatically change the configuration to all the controllers.
	4. The SMS Operator shall be able to:
		1. Assign an ioSmart reader via serial number to a controller door.
		2. Configure input/outputs settings on ioSmart readers.
		3. Configure keypad settings
	5. When an ioSmart reader is configured in RS-485 mode the BLE is activated on the reader template. EntraPass go Pass shall require that the EntraPass go Pass phone be within range of the reader for the EntraPass go Pass to work.
	6. When an ioSmart reader is configured in RS-485 mode the reader shall offer multi-factor authentication to enter the door. Each door shall offer the following options but is not limited to them:
		1. Two-factor authentication not available; uses standard supported smart cards or prox cards.
		2. go Pass biometric; to unlock the door, the cardholder uses the go Pass mobile app to tap the door and enter their biometric phone login. The reader still accepts smart cards
		3. go Pass & disable card reader; to unlock the door, the cardholder uses the go Pass mobile app to tap the door and enter their biometric phone login. The reader does NOT accept any cards.
	7. From the SMS operations screen, the SMS operator shall be able to request the non-programmed ioSmart serial number and the SMS operator shall automatically assign them to the doors.
	8. From the SMS operation screen, the SMS operator shall be able to perform firmware updates on the ioSmart readers.
		1. During the firmware updates the ioSmart controllers shall continue to work.
	9. From the SMS operation screen, the SMS operator shall be able to see the ioSmart reader status such as but not limited to :
		1. Firmware
		2. Tamper state
		3. Memory availability
	10. The Legacy KT-200 and KT-300 shall also support the ioSmart over standard Wiegand protocol using dedicated cables for LED and BUZ.
	11. The operator shall configure the ioModules for the KT-400 or the KT-1 as additional expansion modules.
		1. The ioModules shall communicate with the controllers yusing encrypted RS-485.
		2. The ioModules shall have a serial number that the SMS shall use to supervise activity.
		3. When required the SMS shall upgrade the ioModule firmware.
		4. Each module shall be configurable as 16 inputs or 16 outputs.
		5. The ioModule shall have the following usage options: inputs, outputs, or elevator floors.
5. The SMS shall allow to import KT-400 Standalone and KT-1 Standalone backup into the SMS as a new connection when using a Multi-Site Gateway.
	1. The SMS shall allow to import the following but will not be limited to:
		1. Controller name, programming, networking and MAC settings.
		2. Door names and programming.
		3. Schedule names and programming.
		4. Holiday names and programming.
		5. Action scheduler name and programming.
		6. Cardholder lists and programming.
		7. Cardholder door access rights shall also be imported as door exceptions.

2.4.E Alarm Interface

1. The SMS shall interface with any external alarm system thereby arming or disarming the system by presenting a valid card to an entry/exit door. It also shall be possible to associate a keypad with a reader forcing the cardholder to enter a number in the keypad after presenting a card. This integration shall only be possible with the use of a Multi-Site Gateway. It shall be possible at a minimum to complete the following:

* 1. Set a monitored input as an arming button.
	2. Associate a usage schedule with an arming button.
	3. Set the exit and entry delay.
	4. Determine whether the system must wait for a valid access to arm.
	5. Determine whether the system must wait for a valid access card swipe and appropriate pin number to disarm.
	6. Determine whether the door must relock on arming request.
	7. Associate a monitored input with an alarm panel condition.
	8. Lock a door unlocked by a schedule when armed.

2.4.F Integrations

* + 1. LDAP – Operator synchronization (Active Directory)

The SMS shall interface with the Active Directory (LDAP) for operator management. The SMS shall receive operators from the LDAP system, these operators shall be modified and deleted as required.

1. The SMS shall sync from the Active Directory (LDAP) on a configurable time. Operator changes will flow from LDAP into the SMS. The SMS shall allow operators to force a sync manually instead of waiting for the next sync cycle.
2. The LDAP shall be the authority manager for all operators synced with the SMS.
3. The SMS shall create SMS operators that shall not be synced with LDAP.
4. The SMS shall be able to sync but not limited to the following LDAP fields:
	* 1. Display name
		2. User principal name
		3. User account control (active or inactive).
		4. Password last set
		5. Bad password time
		6. Bad password count
		7. Maximum passwords before change.
		8. Account expiration date
		9. Picture
5. E-mail
	* 1. The SMS shall import as SMS cardholders the LDAP users that are part of a LDAP group and its children groups.
	1. The SMS shall allow for as many security level/EntraPass Workstation configurations as needed. The Active Directory shall send down the proper rights using profiles.
	2. The SMS shall give the option for operators to log in to the SMS manually if active directory credentials do not match.
	3. Certain operators shall be separate from the LDAP sync and shall be managed manually.
	4. The SMS shall manage the LDAP integration from the SMS SmartLink and require a license per LDAP
		1. The SMS shall support up to ten different LDAP connections.
		2. Single Sign On – Operator synchronization (SSO)
6. The SMS shall allow the SMS EntraPass Workstation to offer single sign on when using the LDAP integration.
7. Operators shall simply need to login to Windows using their Windows domain login and open the EntraPass Workstation.
8. The SMS shall also allow manual login to the client software.
9. The need to enter a username and password is not required with single sign on.
	* 1. LDAP – Cardholder synchronization

The SMS shall interface with the Active Directory (LDAP) for cardholder management. The SMS shall receive LDAP users from the LDAP system, these users shall be modified and deleted as required.

1. The SMS shall sync from the Active Directory (LDAP) on a configurable time. Cardholder changes will flow from LDAP into the SMS. The SMS shall allow SMS operators to force a sync manually instead of waiting for the next sync cycle.
2. The LDAP shall be the authority manager for all operators synced with the SMS.
3. The SMS shall allow the creation of SMS cardholders that shall not be synced with LDAP.
4. The SMS administrator shall be able to pair the SMS fields below to the LDAP Attributes. SMS values such as but not limited to the following:
	* 1. Display name
		2. E-mail
		3. Card state
			1. The card state shall be automatically linked to the LDAP “User is Disabled” value and disable or enable the SMS cardholder accordingly.
			2. The SMS administrator shall be able to overwrite the default assignment and provide a custom LDAP numerical attribute instead. This configuration shall ignore the LDAP “User is Disabled” value.
		4. Card numbers one to five.
		5. Card number’s variables such as expiration, date and hour.
		6. Card type
		7. Access levels via the card access groups.
		8. Start/end date
		9. Picture
		10. E-mail
		11. User definable fields 1 to 40
5. When an SMS field is paired with an LDAP attribute, this such field shall be modifiable only from the LDAP. All other SMS fields shall be modifiable from the SMS client
6. The SMS shall allow pairing of any or all fields with the LDAP attributes.
7. Certain SMS cardholders shall be separate from the LDAP sync and shall be managed manually.
8. The SMS shall manage the LDAP integration from the SMS SmartLink and require a license per LDAP.
9. The SMS shall import LDAP users that are part of a LDAP group and its children groups as SMS cardholders.
10. The SMS shall support up to 10 different LDAP connections.
	* 1. Intrusion
11. The SMS shall allow interface with the DSC PowerSeries PC1616, PC1832, PC1864, the MaxSys 4020, DSC PowerSeries Neo HS2016, HS2032, HS2064, HS2128, and the DSC PowerSeries Pro HS3032, HS3128 intrusion alarm panels. This interface eliminates the need for hardwired integration between the SMS controllers and the DSC PowerSeries® intrusion panel.
12. When integrating with the DSC PowerSeries Neo and PowerSeries Pro, the SMS operator shall have the ability to use type 2 or type 3 encryption.
13. With the DSC PowerSeries Neo and the appropriate communication module, the SMS shall connect up to four IP sessions with Kantech controllers. With the appropriate communication, the SMS shall support 1 x RS-232 session and 3 x IP sessions or 4 x IP sessions.
14. With the DSC PowerSeries Pro and the appropriate communication module, the SMS shall connect up to four IP sessions with Kantech controllers.
15. The DSC PowerSeries Neo intrusion panels shall communicate with the Multi-Site Gateway using any of the following methods:
	1. RS-232 mode
	2. TCP-IP or UDP-IP connection.
	3. Global Gateway and KT-NCC.
	4. Directly to a KT-400/KT-1-PCB controller.

With the appropriate communication module the SMS shall allow up to four controller sessions back to one communicator.

* 1. The DSC PowerSeries Pro intrusion panels shall communicate with the Multi-Site Gateway using any of the following methods: a TCP-IP or UDP-IP connection, a Global GatewayKT-NCC, ordirectly to a KT-400/KT-1-PCB controller.

 The SMS shall allow up to four controller sessions back to one PowerSeries Pro.

* + 1. The SMS shall allow for virtual zones integration with the DSC PowerSeries Neo, or the PowerSeries Pro.
		2. The SMS shall trigger DSC zone status based on the access controller event without the need for hardwiring relays or inputs. Zone statuses include alarm, in trouble or tamper.
			1. The SMS shall be able to assign up to 32 virtual zones.
			2. The SMS shall be able to assign up to 32 access controllers from the same Multi-Site Gateway/Global Gateway to one PowerSeries Neo, or PowerSeries Pro (for a virtual zone).
			3. The 32 controllers shall be from any type (KT-300, KT-400, KT-1). The main controller communicating with the PowerSeries Neo, or PowerSeries Pro shall be either a KT-400 or KT-1.
			4. The SMS shall be able to assign one door to one virtual zone,
			5. The SMS shall be able to assign one input (access control) to one virtual zone.
			6. The SMS shall be able to assign access control events to one virtual zone. Event not limited to:
				1. Access denied - Card expired
				2. Access denied - Card lost or stolen
				3. Access denied - Bad access level
				4. Controller tamper
				5. Controller AC failure
				6. Controller low battery
				7. Door forced open
				8. Door open too long
				9. Input in alarm
1. The DSC PowerSeries® and MaxSys series intrusion panels shall communicate with the Multi-Site Gateway using RS-232 connection, or with the Global Gateway/KT-NCC using RS-232 or directly to a KT-400/KT-1-PCB controller.
2. The SMS shall allow for the DSC Maxsys, PowerSeries, PowerSeries Neo, and PowerSeries Pro to perform the following functions:
3. Single and multiple partitions arming and disarming using a reader.
4. Disarm via card only or forced valid card and pin.
5. Single and multiple partitions arming and disarming using operator commands.
6. Receive events from intrusion panel.
7. Receive partition names, user codes and zone names programming.
8. Update user codes.
9. Assign user codes to cardholders.
10. View a fully functional virtual keypad to perform all functions available on the DSC PowerSeries® 1616, 1832, 1864 or the MaxSys 4020 intrusion panel keypad.
11. Control the PGM outputs from a graphic screen with the MaxSys 4020 integration.
12. Bypass zones with the Maxsys 4020, PowerSeries NEO, and PowerSeries Pro integration.
	* 1. Simplex fire event viewing

The SMS shall facilitate an interface with the Simplex 4100ES fire panel thereby eliminating hardwired integration between the SMS controllers and the Simplex 4100ES fire panel. The Simplex 4100ES fire panel shall communicate with the Multi-Site Gateway using RS-232 connection, or with the Global Gateway/KT-NCC using RS-232 or directly to a KT-400/KT-1PCB controller. The SMS shall allow for:

1. View the events coming from the Simplex 4100ES fire panel
2. The events shall be able to be used for but not limited to; reporting, video triggers, and e-mail notifications.
3. View virtual keypad

* + 1. Assa Abloy Aperio wireless locks
1. The SMS shall integrate with Assa Abloy Aperio wireless locks. The integration shall be managed and maintained by the KT-400/KT-1PCB controllers.

1. Up to eight Assa Abloy AH30 hubs shall be able to be put on the KT-400/KT-1PCB over the RS-232 port using a VC-485.
2. The KT-400 shall support four wired doors and eight additional wireless doors. The wireless doors shall not take a slot of the wired doors in the controller memory.
3. The Assa Abloy Aperio wireless locks supported shall be firmware version 2.xx.
4. The KT-1PCB shall support one wired door and two additional wireless doors. The wireless doors shall not take a slot of the wired doors in the controller memory.
5. The SMS shall unlock these wireless doors via licenses. The SMS shall accept licenses in various increments. The licenses shall be distributed to any controller the customer wishes. For example, 96 license package can be divided to the customer’s needs between controllers.
6. The wireless licenses shall be transferable and re-usable within the same SMS. If the customer wishes, they may remove the wireless lock from one controller and attach it to another controller without losing licenses.
7. The SMS shall support one token for every 1 to 16 wireless locks. The tokens shall only be needed for updating the software. Enforcing tokens to maintain the integration within the same version shall not be accepted.
8. The day to day operations such as but not limited to access granted, access denied, door forced open, door open too long, shall be managed locally by the KT-400 and KT-1PCB. The need for the SMS software to generate the access granted shall not be accepted. The KT-400 and KT-1PCB shall be the authorities state for the cards and locks
9. The wireless locks shall still work with 100,000 cards even if the SMS is not communicating with the access controller.
10. To conserve battery on the Assa Abloy Aperio locks, the lock shall only wake up when a wireless door action/event is generated. The wireless door shall transmit an event to the controller and SMS within one second.
11. The wireless locks shall be shown as standard doors/readers in the SMS. From the SMS clients the customer shall be able to assign the wireless locks in access levels for the users, door access exceptions, groups, SmartLink task and others. The customer shall be able to see real time status of his doors and run reports similar to the wired doors.
12. The SMS shall allow wireless lock integration with KT-400 and KT-1PCB with the Multi-Site Gateway, the global windows gateway and the KT-NCC.
13. The wireless locks shall allow triggering KT-400 and KT-1PCB relays on specific access or door events. The wireless locks shall support at a minimum:
	1. HID cards proximity and HID iCLASS smartcards.
	2. The IN100 v3 locks shall also support ioProx XSF cards.
	3. PIN numbers
	4. Relay activation on the following events:
		1. Door forced
		2. Door open too long
		3. Door alarm relock
		4. Invalid card status
		5. Bad access level
		6. Other access denied
		7. Access granted
		8. Card trace
		9. Extended door access delay.
	5. Unlock schedule with first man in.
		1. Must be woken up to schedule to start and end.
	6. Secondary REX
		1. Must be woken up for the secondary REX to take effect.
14. When connected to the global Windows gateway and KT-NCC the wireless locks shall support:
	1. Event relay actions
	2. Global virtual alarm system.
	3. Secondary access levels
15. The SMS shall allow manual operations on the wireless doors. The action on the door shall only take effect when the wireless door wakes up and transmits to the KT-400 or KT-1PCB based on local access or door event. A local door event shall also need to lock or restore the door to its normal state. Manual operations allowed shall be but not limited to:
	1. Unlock/lock door
	2. Door back to schedule.
	3. Temporary unlock
	4. One time access
	5. Enable/disable reader
16. With the IN100 v3 locks the SMS shall allow for the lock to report periodically and update it status based on the KT-400 or KT-1PCB door programming.
17. In addition to the standard access and door events, the SMS shall receive specific events and status from the AH30 hub and the wireless locks. The following specific events shall be available but will not be limited to:
	1. Communication failure
	2. Device online/offline
	3. Radio disturbance
	4. Battery flat/low/ok
	5. Device tamper
	6. Door state
	7. Lockstate: Unlocked/locked/secured/jammed
	8. Handle state: Used/not used
	9. Key cylinder state

2.4.G Virtual Alarm System

1. The SMS shall include an alarm system function to automate building supervision. As a result, no module or additional electronic equipment shall be required. Each partition shall have a reader or group of readers that will be used to arm, disarm, or delay the arming of a supervision point or group of points within the partition. Partitions can be programmed to arm via reader only, input only, or reader and input.
2. When arming from reader connected to a KT-400 or KT-1 controllers, it shall be possible to arm via multi-swiping the card on the reader (double or triple swipe).
3. The SMS shall allow for the creation of over 100 partitions per Global Gateway or KT-NCC. It shall be possible to define the following programming parameters:
4. A name
5. A delay duration
6. An entry and exit delay.
7. An activation time for the alarm siren.
8. A maximum number of delays.
9. An access level required to arm/disarm.
10. An arming, disarming, and delay group of readers.
11. A reader or group of readers that will be disabled when the area is armed.
12. A door or group of doors that will be locked when armed.
13. Arm one or more partition from one reader.
14. Associate a supervision point(s) to one or more partition at one time.
15. Associate one or more alarm relays with a partition.
16. Associate a time zone.
17. Associate eight DSC PowerSeries PC1616, PC1832, PC2864, PowerSeries Neo or MaxSys 4020 partitions to be armed or disarmed.
18. The SMS shall make it possible to associate an automatic arming schedule for each partition. It shall be possible to manually arm, disarm, or delay arming a partition or group of partitions from a EntraPass Workstation. An audible signal shall warn the operator during an alarm.
19. The SMS shall allow the option for cardholders to swipe their card and enter their pin number to disarm. The SMS shall not force cardholders to enter their pin number when the virtual alarm system is disarmed; unless required.

2.4.H System Section

1. The SMS shall define the profile of a system operator based on name, password, language, privileges, login schedule, security level, workspaces, and password expiry date. The SMS shall provide the possibility to force the operators to assign a mandatory card type to the users. The operator shall be able to provide a default card.
	1. The SMS shall allow to send a welcome e-mail to the SMS operator.

The SMS shall allow the SMS operator to re-send the welcome e-mail as needed.

This welcome e-mail shall include links to automatically pair the SMS operator with the following SMS applications:

Link to download EntraPass web.

Link to download and pair the SMS operator automatically to EntraPass go for Apple® and Android® devices.

Link to download and pair the SMS operator automatically to EntraPass go Install for Apple® and Android® devices.

* 1. If required, the operator can customize the SMS welcome message with different e-mail headers and footers.
1. The SMS shall allow to configure for each operator their Web/mobile rights:
	1. Allow to login to Web/mobile.
	2. Default message list filter.
	3. Default message filter buffer upon login.
	4. Concurrent login option.
	5. Session timeout on idle timer.
2. The SMS shall offer the option for the SMS administrators to force strong passwords for operators. The strong password settings shall be configurable by the SMS administrators.
3. When in the operator, or operator and EntraPass Workstation alarm management mode, each operator shall be given a priority to receive the alarms. Active operators with the lowest priority shall receive the alarms first.
4. Operators shall have the option of always or never, to receive alarms.
5. The SMS shall determine access rights granted to an operator based on security levels. There shall be three predefined access levels called installer, administrator, and guard. The SMS shall have the ability to create an unlimited number of security levels that can be assigned to one or more operators. It shall be possible to determine from which system components the operator shall be authorized to receive events and take action. It shall be possible to specify for each programming window if the operator can (any combination):
	1. View the component in read only.
	2. Add new components
	3. Modify existing components (cannot add new).
	4. Delete components
	5. Save as
	6. Print components
	7. View links
6. The SMS shall allow system administrators to grant or deny operators access to all system physical components such as gateways, sites, controllers, doors, relays, inputs, access levels, reports, schedules, tenant lists, video servers, card types using workspaces. This allows greater ease for larger sites to locate and assign components that pertain to specific gateways and sites. System administrators shall be able to tailor specific system applications and EntraPass Workstations workspaces, therefore restricting access to information to all levels of operators. Operators shall be able to use temporary workspaces to narrow their fields of view when accomplishing specific tasks, and then easily revert back to their main workspace.
7. The SMS shall allow the configuration of a system wide feature that will automatically disable an operator that has not logged in at least once in X days.
	1. The SMS administrator shall have the option to customize the inactivity timer from 30 days to 365. The SMS feature can also be turned off by the SMS administrators
	2. The SMS shall automatically notify the operator via e-mail 10 days prior to the deactivation.

2.4.I Report Section

1. The SMS shall include templates for various types of reports to include the following:
	1. Card use reports
	2. Manual operations reports
	3. Alarm reports
	4. Historical reports
	5. Time & attendance reports.
	6. Detailed reports
	7. Summary reports
	8. Statistical reports
	9. Muster reports
	10. Roll call reports
		1. The SMS shall allow for the creation of custom reports based on any event or component in the system. The SMS shall support an unlimited amount of customized reports.
		2. All reports shall be able to be displayed on screen, printed, or sent by e-mail on a daily, weekly, or monthly basis. All event reports can be automated to be generated and sent at a specific time for a specific time period.
		3. The SMS shall support at a minimum the following report formats: Sybase, Dbase IV, CSV, XLS, PDF, RTF, and TXT.
		4. The SMS shall be able to generate an access report in CSV with all the card information associated to that access event.
		5. All component modification events shall be tagged with addition (+), modification (=) or deletion (-) tag. In all event driven reports the operator shall have the choice to specify a tag or all tags in order to further filter report.
		6. The system shall support for the creation of custom time and attendance reports. Each time and attendance report shall support up to 32 rules for masking the entry and exit times of each card. Also each report shall support a “First entry and last exit” feature.
		7. The SMS shall allow the creation of custom roll call reports, which can without operator intervention be e-mailed to multiple people, and/or printed on multiple printers. The roll call report shall be a system wide feature.
		8. Each report quick report, historical report and time attendance report shall have a priority number assigned to it. When multiple reports are requested the SMS shall prioritize the creation of the report based on their priority number. From the report queue management window the operator shall have the possibility to promote the report to a higher priority. The operator shall also have the ability to request more processing power form the computer in order to expedite the report creation.
		9. Reports shall be prioritized from queue of 1 to 99. When the report is requested as priority one it shall be processed first. The default value for all new reports shall be set to 50. Operators shall be able to change it as needed.
		10. The SMS shall allow the creation of custom muster reports, which can without operator intervention be e-mailed to multiple people, and/or printed on multiple printers. The muster report shall portioned by Global Gateway or KT-NCC.
		11. The SMS shall have a statistical window showing all reports executed, the time of execution, time lapse, number of events, requestor, and application request. The report shall be exportable in CSV format.

2.4.J Audit Trail Reporting

1. The SMS shall include the ability to track all specific field changes made by the operators. The following events are the minimum the SMS shall track:
	1. The operator that made the change.
	2. The time the change occurred.
	3. The component that was changed.
	4. The field that was changed.
	5. The value of the field prior to the save.
	6. The value of the field after the save.
2. If required, the SMS administrator shall track specific components or even the entire database. The following list of components are trackable, but the SMS is not limited to the them:
	1. Access level groups.
	2. Access levels
	3. Cards
	4. Card types
	5. Badges
	6. Action scheduler
	7. Schedule and holidays.
	8. Tasks and SmartLink triggers.
	9. Hardware programming (devices)
	10. Graphics
	11. Areas
	12. Virtual alarm panels
	13. Report templates
	14. Operator, security level, and workspaces.
3. To view the exact details of the modification transactions the SMS operator shall click the audit trail button and select the needed transaction. The following is a list of the transactions but the SMS is not limited to this list:
	1. Data type (text, numerical, date, boolean).
	2. Modification date
	3. Operator name (that did the modification).
	4. Reference type
	5. Field name (column name in database).
	6. Field description (GUI label name).
	7. Old value
	8. New value
4. To view all changes performed by an operator, the SMS shall provide a filter to generate a transaction report. Choose from the following options:
	1. Date range
	2. Component type
	3. Operator
5. To export all the changes of a specific component, the SMS shall providea transaction report in a CSV format. . Each row shall represent one transaction and shall include all required information.
6. In a CSV format report, it shall be possible to export one modification or all modifications from that component.
7. The SMS shall be capable of storing up to five years of transactions. It shall be configurable by the SMS administrator

2.4.K Options Section

1. The SMS shall allow operators to access basic server and display functions and allow the operator to determine default settings for the server hard drive. The operator shall also be able to determine the time to perform a server backup, programmable on monthly, weekly, or daily basis. It shall be possible to schedule and plan mass automatic KT-400 or KT-1 firmware updates.
2. The SMS shall allow for the servicing company to enter their contact information for the SMS operators’ disposal.
3. The SMS shall allow system administrators to put the SMS in a read-only mode. When the SMS administrator puts the SMS in read-only mode, the SMS operators are visually notified. In addition, SMS operators can no longer perform changes or add components in the SMS. The SMS operators are allowed to receive events, perform door operations such as but not limited to unlocking, locking, and temporary unlocking.
4. The SMS shall allow system administrators to put the SMS in a maintenance mode. When the SMS administrator puts the SMS in maintenance mode, the SMS operators shall be able to perform their regular actions based on their rights but would not receive pop-ups and real-time e-mail notifications.
5. The SMS shall allow system administrators to easily migrate ioProx extended facility code secure format (XSF) cards from a seven character HH:DDDDD to a HHHH:DDDDD format without downtime.
	1. The SMS shall allow the system administrator to convert automatically all ioProx XSF cards to an extended facility code secure format of their choosing. The SMS shall change all the card programming instantly.
	2. The SMS shall allow the system administrator to run a conversion tool that will convert ioProx XSF and ioSmart cards in real time into their proper extended facility code secure format without having any down time.
		1. This process shall have the option to be turned on or off as the system administrator wishes.
		2. The cardholder would need to swipe the card twice the first time once the process is started.
		3. The conversion shall be in real time and take less than 1 second per card to occur.
	3. The SMS extended facility code secure format conversion is optional, as the SMS shall have the option to run as standard HH:DDDDD or other formats supported.
6. To reduce unwanted clutter in the SMS database; components that have been deleted for X amount of years shall be automatically purged from the database.
	1. The SMS shall allow deleted computer retention from one to five years.

2.4.K Help Section

1. The SMS shall have a contextual help button in every window. The operators shall also have the option of pressing F1 on their keyboard and the help window will appear with the correct section of the item they were looking at in the SMS.
2. The SMS shall include an about window which shall include basic information about the SMS. It shall also include the KAP start/end date and tokens needed. The operator shall be able to send KAP details via e-mail to a pre-defined e-mail list by the click of one button.
3. In addition the about window shall include contact information for the SMS manufacturer and contact information for the installation company/dealer. In addition the SMS shall support to identify the SMS to the customer with his contact information. The dealer information shall include at a minimum but not limited to the following:
4. Company name
5. Address
6. Website link
7. E-mail link

2.4.L System Status Section

1. The SMS shall allow operators to view the state of various access system components in text or numerical form. A specific controller’s state shall also be able to be viewed in graphic form using the picture of the controller with the status of each terminal. EntraPass Workstation and database status shall also be able to be displayed.
2. The SMS shall offer an active status count of all operators in the SMS.
	1. The SMS shall offer the ability to run reports on login counts so that operators can run trends on operator peak usage.
3. The SMS shall offer the ability to have a window displaying all the current logins in the SMS. The SMS logins shall be filterable and sortable by type of application such as web, mobile, EntraPass Workstation or database applications.
	1. The SMS shall allow the operator to force logout operators thus ending immediately their sessions in the EntraPass Workstation, Web and mobile clients
	2. The SMS shall allow the operator to force logout and permanently disable the operator thus ending immediately their sessions in the EntraPass Workstation, web and mobile clients. The operator won’t be able to login until reactivated manually.
	3. The list shall be exportable in CSV file format.

2.4.M Various Tools

1. The SMS shall employ an express setup to configure system components such as sites and controllers, as well as peripherals associated to these components such as ports and inputs. This utility will reduce the programming time to a minimum.
2. The SMS shall employ a database utility to allow the re-indexation and verification of archived files and verify the integrity of indexes, links, and database arborescence.
3. The KT-Finder tool shall help troubleshoot the Kantech IP Link, KT-400, KT-1 and KT-NCC on site or remotely. It can also be used as an alternate method of configuration for both.
4. The SMS shall include a vocabulary editor to be used in designing custom language dictionaries.

2.4.N Video Vault

1. Video vault is an optional remote networked application used to automate the recovery of video data from the DVR/NVR and save it on a disk for long-term video storage and retrieval. The information can be stored on an independent system, or within the server. The footage that shall be tagged and recoverable from the DVR/NVR shall include SMS triggers, manual triggers, and saved video server footage.

2. For the archived video files it shall be possible to complete the following:

1. Assign a folder name to index the archived files.
2. Create sub folders based on the day of the week, day, week, month of the year, month, video server name, camera name and/or event description name.
3. Determine the hard drive to store the recovered videos.
4. Determine the composition of the name of the saved file.
5. Determine the format of the saved video.
6. Assign a frame from the saved video to represent as a saved file.
7. Determine the number of simultaneous downloads.
8. Determine a size limit for recoverable videos.
9. Assign a password to videos stored.
10. Determine a delay between requests to the server.
	* 1. There shall be scheduled transfers for archiving to reduce video network traffic during peak times.
		2. Create a sub folder to divide the stored video in logical folders. The sub folders shall be based on day of the week, week, and month of the year.
		3. The operator shall have the ability to configure the SMS to send an e-mail with four thumbnail images of the alarm.
11. The e-mail contains four thumbnail images that capture the following time stamps:
* Five seconds before the alarm.
* The alarm.
* Two seconds after the alarm.
* Five seconds after the alarm.

**2.5 PERFORMANCE – WEB/MOBILE APP**

2.5.A EntraPass web

1. EntraPass web shall be an optional tool that will provide an interface to perform certain functions from a remote location to be used with the regular SMS system.
2. EntraPass web shall be based on Microsoft, Windows Presentation Foundation (WPF) and be a download application from the main web server. The operator shall run EntraPass web from his desktop.
3. EntraPass web shall be updated automatically when the main web server is updated.
	1. Manual updating of EntraPass web shall not be supported.
4. EntraPass web interface shall allow the operator to have a favorite list of connections. The operator shall be able to select from the favorite list of servers and login. A user name and password shall be required for each one.
5. EntraPass web operator transactions involving modifications and operations shall be sent to the SMS in the local time zone of the operator.
6. EntraPass web shall offer the following operations:
	1. Operator specific security rights. The SMS EntraPass Workstation shall allow configuring operators to be able to access EntraPass web. It shall also allow the operator’s security rights and workspaces to be used on the web or mobile. An operator that cannot add cards on the SMS EntraPass Workstation shall not be able to do the same the EntraPass web
	2. Automatically adjust the operator’s language selection. The language selection shall be done at the creation of the operation in the SMS EntraPass Workstation. The languages supported shall be English, French, Spanish, Italian, Portuguese, Simplified Chinese, Dutch, Turkish and German.
	3. There shall be no limit to the amount of EntraPass web applications that can be installed.
	4. Shall not require any kind of refreshing to receive any new data.
		1. Refreshing the “page” shall not be supported.
	5. EntraPass web licenses shall be managed by concurrent active logged on sessions.
		1. The need to have dedicated licenses per computer shall not be supported.
	6. Shall support a right-click action to allow additional functions.
7. EntraPass web shall have a complete, easy to use and intuitive look and feel.
8. EntraPass web shall allow the following for door, relay and input menus:
	1. Shall allow the operator to select multiple components using the SHIFT/CTRL buttons on the keyboard and the mouse.
	2. Shall allow the operator view real-time status of the components. Systems requiring a manual refresh shall not be acceptable.
	3. Shall allow the operator to search for a particular component within the site. The search filter shall update the results as the operator types.
	4. Shall remember the last site visited and load the same site when revisiting the menu.
	5. On doors the operator shall be able to:
		1. Unlock/lock a door.
		2. One time access (pulse door).
		3. Temporary unlock
		4. Return the door to schedule.
		5. Enable/disable exit/entry readers separately using the same door icon.
		6. Arm/disarm door when using the KT-400, KT-1 and alarm panel.
		7. View full text status.
		8. Enable/disable floors when programmed as elevator.
		9. Change unlock schedule of the door.
		10. Clear unlock schedule of the door.
	6. On the relays the operator shall be to:
		1. Activate
		2. Deactivate
		3. Temporary activation
		4. Return door back to schedule.
	7. On the inputs the operators shall be to:
		1. Normal supervision
		2. Continuous supervision
		3. No supervision
		4. Temporary no supervision
9. EntraPass web shall provide complete card management.
	1. EntraPass web shall learn and remember the operator’s screen settings.
		1. It shall be possible to see all settings of the cardholder at once without the need to use tabs.
		2. It fields shall be grouped in a logical order to allow operator to completely accomplish their tasks without move around the window.
	2. EntraPass web shall support up to a total of 13 access levels for each card user per Global Gateway or KT-NCC. Each access level can have its own expiry date.
	3. EntraPass web shall support up to a total of five access levels for each card user per site/connection when using the Multi-Site Gateway. This feature shall be available with the KT-400 and KT-1. The SMS shall advise the operator if doors are not supported when adding additional access levels (two to five).
	4. EntraPass web shall allow adding door access exceptions to the cardholder’s list of access rights.
	5. EntraPass web shall configure every aspect of the card that the EntraPass EntraPass Workstation offers.
	6. EntraPass web shall allow for operators to manage the user’s go Pass.
	7. EntraPass web shall allow for operators to manage the user’s HID mobile credentials.
	8. EntraPass web shall allow the operator to print badges using dye-sublimation printers (badge printers).
		1. The operator shall be:
			1. Able to assign a badge template to a user.
			2. Able to preview both sides of the card printing.
			3. Assign a badge printer to print on.
			4. Print both sides, back side only or front side only.
	9. EntraPass web shall facilitate the following additional operations for the cardholder:
		1. Linking a cardholder to a tenant list for the KTES
		2. Import and take a picture of the cardholder using a web cam.
		3. Viewing a list of cardholders in a list.
		4. The cardholder list shall be configurable to include cardholder information. It shall also allow to sort by the columns.
		5. The cardholder list shall allow a right click function to modify or delete the cardholder.
		6. Searching by card number, username and user definable fields.
		7. Importing and exporting cardholders using CSV.
		8. Viewing all doors assigned to a cardholder regardless of access levels.
			1. The door list shall be printable and exportable in PDF or EXCEL (XLS) formats.
10. EntraPass web shall support up to 999 action schedulers. These action schedulers shall allow the user to perform actions on the SMS controllers within a pre-defined timeframe.
	* 1. Each action scheduler shall allow up to eight different component triggers. These components can be from the same controller, or a different controller.
		2. The action scheduler shall be stored in the KT-400, and the KT-1. When EntraPass web programs the action scheduler, the controller shall not need the SMS to trigger the action scheduled.
		3. With the SMS global windows gateway or KT-NCC is connected, the action scheduler shall be stored the on the SMS global windows gateway, or the KT-NCC making the action scheduler available for all SMS controllers.
			1. The action scheduler shall allow but will not be limited to the following features:
				1. Toggle door unlock.
				2. Unlock door
				3. Relock door
				4. Temporarily unlock door.
				5. Activate relay
				6. Deactivate relay
				7. Temporarily activate relay.
				8. Arm door partition.
			2. The action scheduler shall be scheduled to trigger at limited intervals but will not be limited to these intervals:
				1. Once on a specific date and time.
				2. Daily at a specific time until a specific date.
				3. Weekly at a specific time until a specific date.
			3. EntraPass web shall also allow the EntraPass web to trigger a task (task builder) within the action scheduler.
			4. These tasks shall be SMS dependent but can trigger anything configurable in the SMS tasks.
			5. Operators can easily see upcoming action schedulers.
			6. The SMS operator shall be able to see if the action scheduler is a one-time action or a reoccurring action without having to open the action scheduler.
11. EntraPass web shall provide complete access level management.
	1. EntraPass web shall allow the operator to customize his access level list to show more access levels in columns in order to provide a better view of the access levels.
	2. EntraPass web shall provide a preview on how the access level is programmed.
		1. It shall be possible to zoom in on the access level preview and see down to the hour how the access level is programmed.
	3. EntraPass web shall allow operators to add quickly a door to a list of access levels.
		1. The operator shall select a door and see a list of access levels.
		2. EntraPass web shall return to the assigned door shown on the schedule. If the door is not assigned to an access level, it shall show, none.
		3. The operator shall be able to change any of the doors assigned access levels by simply changing the schedule.
12. EntraPass web shall provide complete schedule management.
	1. EntraPass web shall allow the operator to customize his schedule list to show more schedules in columns in order to provide a better view of schedule.
	2. EntraPass web shall provide a preview on how the schedule is programmed.
		1. It shall be possible to program quickly the schedule by either entering the times or using a scroll bar.
		2. It shall also be possible to quickly program the days by choosing them manually or selecting pre-defined day templates.
13. EntraPass web shall provide complete holiday management.
	1. EntraPass web shall allow the operator to customize his holiday list to show more holidays in columns in order to provide a better view of holidays.
	2. EntraPass web shall provide a preview on how the holiday is programmed.
		1. It shall be possible to program the holiday date, and observe the holiday using the drag and drop function.
14. EntraPass web shall provide complete tenant and tenant list management.
	1. EntraPass web shall allow the operator to customize his tenant list to show more tenant lists in columns in order to provide a better view of tenant lists.
	2. EntraPass web shall provide a facility for complete tenant programming in an easy to use GUI interface.
	3. It shall be possible to see all settings of the tenant at once without the need to use tabs.
15. EntraPass web shall allow for map management.
	1. The Operator shall be able to use easily and intuitively the map creation tool to import floor plans or maps in the EntraPass web. The image formats support shall be JPEG and GIF.
	2. The operator shall have the ability to place components on specific parts of the map and assign double click actions.
	3. The operator shall be able to view maps from their screen.

* 1. The operator shall be able to do the following:
		1. See real time visual status of a component. At a minimum the following components shall be available:
			1. Doors and elevators
			2. Inputs
			3. Relays
			4. Map links
			5. Virtual keypad
			6. Controller
			7. Video Cameras
		2. Double click on the component to perform actions.
		3. Right click on the component and choose a different action.
		4. Quickly move to different maps by using links.
		5. Maximize the map. EntraPass web shall be able to keep the visual aspect ratio.
	2. EntraPass web shall remember the last map used and load it so that operators do not need to always choose a map to start.
	3. The operator shall be able to modify the assigned door schedule from the map.
		1. The operator shall not need to have access to the entire door to be able to change the assigned door schedule.
		2. Changing the door schedule shall be a privilege that can be turned on or off by the SMS administrator per operator
1. EntraPass web shall allow for operator programming and management.
	1. EntraPass web shall allow to create, modify, delete and view operators.
	2. EntraPass web shall allow the following but is limited to operator management:
		1. Operator display name
		2. Operator login name
		3. Operator password following the SMS password complexity rules.
		4. Language
		5. Security level
		6. Workspace
		7. Password reset
		8. Password last set every X days.
		9. Disable operator X consecutive bad logins.
		10. Maximum passwords before change.
		11. Account expiration date.
		12. Picture
		13. E-mail
		14. Disable operator
		15. Welcome e-mail settings
	3. EntraPass web shall allow to send a welcome e-mail to the SMS operator.
	4. EntraPass web shall allow the SMS operator to re-send the welcome e-mail as needed.
	5. This welcome e-mail shall include links to automatically pair the SMS operator with the following SMS applications:
		1. Link to download the EntraPass web.
		2. Link to download and pair the SMS operator automatically to EntraPass go for Apple® and Android® devices.
		3. Link to download and pair the SMS operator automatically to EntraPass po Install for Apple® and Android® devices.
2. EntraPass web shall provide video integration with the American Dynamics HDVR and VideoEdge (NVR), INTEVO Advanced, INTEVO Compact and Exacq A, Z, ELS, ELXS, ELX-IP, ELX-SR, LC, LC-IP series DVR/NVR products.
	1. EntraPass web shall allow the operator to complete the following:
		1. To create and manage video views.
		2. To select a single cameras and drag them in the viewing screen to view live video.
		3. To select a predefined video view and drag it in the viewing screen to view live video.
		4. The video cameras shall be able to be viewed without the need to create video views.
		5. To select nine different video camera layouts.
		6. Support up to 16 cameras at once per view.
		7. To video search for up to one hour.
		8. To video search exporting in watermarked or AVI format.
			1. The watermarked format shall include a video player embedded in the clip.
		9. To video search using metadata to only show alarm clips based on camera motion alarms or access event video recording clips. Thus speeding up finding video alarms for the customer.
		10. To PTZ control a camera using the mouse or computer keyboard (arrows for pan/tilt and +/- for zoom in/out).
			1. The PTZ shall offer three speeds based on mouse movement.
3. EntraPass web shall allow the operator to generate reports:
	1. All reports shall be sent using e-mail to multiple e-mail addresses in an Abode PDF file, or Microsoft Excel file.
	2. Reports shall also be able to be viewed on EntraPass web. The operator shall still be able to use EntraPass web while a report is generating.
	3. Reports viewed on screen shall allow the operator to save the report in an Abode PDFfile or a Microsoft Excel file.
	4. Reports shall allow additional filtering within the report values to better accommodate report filtering.
	5. EntraPass web shall allow generating quick reports.
		1. Quick reports are pre-defined event templates that operators can choose from. The operator shall be able to select multiple event templates.
		2. The quick reports shall offer the following pre-configured event templates:
			1. All events
			2. Access events
			3. Alarm system events
			4. Area events
			5. Camera events
			6. Controller events
			7. Database events
			8. Door events
			9. Guard Tour events
			10. Input events
			11. KTES Events
			12. Operator events
			13. Relay events
			14. Server based events
			15. Time and attendance based events.
			16. Video server based events.
		3. The operator shall have the ability to choose a specific timeframe based on date and time.
	6. EntraPass web shall allow generating custom reports.
		1. Custom reports shall be built in the SMS EntraPass Workstation and can be used on EntraPass web.
		2. The operator shall have the ability to choose a specific timeframe based on date and time.
		3. There shall be no limit of custom report available to the operator.
	7. EntraPass web shall allow generating user list based reports.
		1. The operator shall be able to quickly filter the user list based on the following:
			1. The entire card database.
			2. Based door access
			3. Card type assigned
			4. Access level assigned
		2. The operator shall also be able to filter the report based on:
			1. One user definable field with a search value.
			2. Card status.
				1. Enabled/disabled
				2. Lost/stolen
				3. Postdated
				4. Expired
				5. Suspended
			3. Comments
			4. Card traced
			5. To be deleted when expired.
			6. Wait for PIN
			7. PIN search
		3. Allow the operator to choose which values in the report to include. These values should include but not be limited:
			1. Username
			2. Card number
			3. Card type
			4. Card filter
			5. Picture
			6. Access level
			7. Card information fields (selectable).
			8. Card state
			9. Start/end date
			10. Count values
			11. Card parameters
	8. EntraPass web shall allow generating a doors “assigned to” report:
		1. The operator shall be able to quickly filter the report based on the following:
			1. Based on the access level.
			2. Based on the card type.
		2. The operator shall be able to select which component (access levels or card types) the report will include.
		3. The report output shall include the access level or card type name and the doors associated with the schedule.
4. EntraPass web shall allow the operator to view events in real time.
	1. EntraPass web shall allow the operator:
		1. To view events in real time. Each event at a minimum shall include:
			1. Date and time
			2. Event name
			3. Description of the component.
	2. The event viewer shall support natively a swipe and show feature. The picture of the cardholder shall appear on access related events.
	3. On pre-defined video alarm recordings, a video button shall appear on the event screen for each event that has video alarm.
		1. The operator shall be able to click on the button to view the alarm video clip.
	4. From the event viewer the operator shall be able at a minimum to:
		1. Able to search for any event, date, time, description using the filter field.
		2. Able to sort by date/time, event and description.
5. EntraPass web shall allow for the DSC PowerSeries, Maxsys and Simplex Fire 4100ES virtual keypad to be used. From the maps, or dedicated menu the operator shall easily be able to bring up a fully functional DSC virtual keypad and perform all actions allowed by the DSC PowerSeries 1616, 1832, 1864 keypad and Maxsys keypad.

1. EntraPass web shall allow for the DSC PowerSeries, Maxsys, PowerSeries NEO, and PowerSeries Pro operators to complete the following actions:
	1. View partition status
	2. Arm and disarm partitions.
	3. View zones status
	4. View and control the virtual keypad from the DSC PowerSeries 1616, 1832, 1864 and Maxsys.
2. EntraPass web shall allow for the programming of Kantech hardware.
	1. The EntraPass web shall support but not be limited to programming the following:
		1. Sites
			1. Naming a site
			2. Adding user definable fields, to best describe the sites.
			3. View linked connections
		2. IP connections
			1. IP link
			2. KT-400 IP
			3. KT-1 IP
			4. KTES IP
		3. Direct connections
			1. USB or Serial
		4. Controllers:
			1. KTES
			2. KT-100
			3. KT-200
			4. KT-300
			5. KT-400
			6. KT-1
		5. ioSmart readers configuration in the controller menu.
			1. Configuring ioSmart Readers to the KT-400 and KT-1 controllers.
				1. Assigning an ioSmart reader via serial number to a door.
				2. Configuring Input/outputs settings on ioSmart readers.
				3. Configuring keypad settings
		6. ASSA ABLOY Aperio wireless locks configuration in the controller menu.
			1. Associate the Aperio wireless lockset to a door for the KT-400 and KT-1.
		7. Component
			1. Door programming including but not limited to:
				1. Multi-swipe settings
				2. Intrusion arming/disarming
				3. Unlock/open settings
				4. Door contact and REX settings.
				5. Schedule assigned
				6. Door naming
				7. First person in with grace period.
				8. Exit/entry readers per door with KT-400.
			2. Relay programming including but not limited to:
				1. Activation schedule
				2. Disable relay schedule
				3. Temporary activation timer
				4. Relay naming
			3. Input programming including but not limited to:
				1. Monitoring schedule
				2. NC/NO status
				3. Relay activation settings
				4. Input name
			4. Firmware update requests to the controllers so that the SMS shall update them to the latest firmware provided.
	2. When using the KT-1 with the auto-enrolment feature.
		1. The auto-enrolment shall work on a local LAN segment of the network.
		2. EntraPass web shall display a dedicated list of all unassigned KT-1s. Using EntraPass web the operator shall pick the KT-1 they are interested in.
		3. EntraPass web shall allow the following using the auto-enrolment wizard:
			1. Assign a KT-1 to a site.
			2. Name the door
			3. Activate the exit reader.
			4. Activate the door contact.
			5. Activate the request to exit.
	3. EntraPass web shall support a quick, intuitive, and easy to use express setup to configure controllers and their doors, relays and inputs.
	4. The operator shall be able to manually modify, delete or add components after the express setup.
	5. The operator shall be able to, at a glance, see in a visual and easy to understand, the site communication time, communication status and how many controllers are communicating.
		1. The operator shall also be able to see per controller the communication status.
3. EntraPass web shall provide e-mail notification and alarm management with the watchlist.
	1. EntraPass web shall have the ability to select manually which door, relay, input and elevator to watch for abnormal events.
	2. The operator shall be able to see watchlist events regardless of the time zone difference between the event and the EntraPass web instance.
	3. A watched component shall generate an alarm on EntraPass web. The operator shall have a dedicated column (watchlist) where all the alarms will appear as bubble-color-coded events with text.
		1. Each event shall be categorized with the appropriate color by the SMS.
	4. The operator shall be able to able to complete the following actions:
		1. Right-click on the event and go to associated:
			1. Component
			2. Video recording
			3. Map
		2. Scroll back to the first alarm since he logged in to EntraPass web session.
		3. Shall be able to tag a watchlist with e-mail notification also
4. EntraPass web shall provide tabs similar to a web browser.
	1. The operator shall be able to create unlimited tabs.
	2. Each tab shall be customizable to the operator’s specifications. A tab can be customized to have any of the following two features configured, but will not be limited to this list:
		1. Schedule management
		2. Access level management
		3. Holiday management
		4. User management
		5. Tenant management
		6. Door/elevator operations
		7. Relay operations
		8. Input operations
		9. Events
		10. Maps
		11. Video viewing
		12. Reports
		13. Action Schedule
		14. Hardware setup
	3. Each tab shall perform the following functions:
		1. Become a floating tab to use on multiple screens, or embed in EntraPass web.
		2. Shall remember the last map used so that operators do not need to reselect the map.
		3. Option to split each tabl into two to display two features in a horizontal or vertical layout.
	4. The operator shall have the ability to open unlimited tabs at the same time.
5. EntraPass web shall at a minimum be supported by any web browser and Windows® OS.
6. The SMS administrator shall be able to change the splash screen title and image of the login page, and the highlight color of EntraPass web.

2.5.B Mobile app - EntraPass go

1. The mobile app is an optional tool that will allow performing certain functions from a remote location to be used with the regular SMS system via iPad, iPhone, Android phones and Android tablets. The mobile app provides card management to guards, secretaries, or managers without the need to deploy a full EntraPass Workstation. A concurrent connection option shall provide access to a predetermined number of users.
2. The concurrent connections are shared with EntraPass web connections.
3. The EntraPass go operator transactions involving modifications and operations shall be sent to the SMS in the local time zone of the operator.
4. The mobile app shall have the ability to be viewed in multiple languages. The mobile app shall be available in English, French, Spanish, Italian, Portuguese, Simplified Chinese, Dutch Turkish and German. The languages shall be preselected based on the device language.
5. The following functions are available using mobile app:
6. Card management (including five cards per username) including but not limited to.
	* + 1. Card names
			2. Card numbers
			3. Card expiry hour
			4. Go Pass management
			5. Access levels
			6. User pictures
			7. Access levels
				1. Secondary with expiration date when using a Global Gateway.
				2. Additional access level when using a Multi-Site Gateway.
				3. Access door exceptions
			8. Forty card fields to best describe the user.
			9. Start/end date
			10. PIN
7. Live cardholder picture capture using a camera.
8. Create, modify and delete access levels.
9. Create, modify and delete schedules.
10. Assign access levels
11. Perform door operations
12. Change the unlock schedule of the door.
13. Perform relay operations
14. Perform input operations
15. Perform elevator operations
16. Request historical or quick reports using e-mail.
17. View live events using the menu or the quick launch viewer.
18. Search for events using text filters.
19. Arm and disarm DSC partitions.
20. View DSC zone status.
21. For VideoEdge, Exacq, or INTEVO video management systems:
	* + 1. Live video view in portrait and landscape mode.
			2. Video search
			3. Video alarm clip view on access events. When video is available on the access or DSC event, a camera icon shall appear and operators shall be able to click on this icon and view the video alarm.
22. The mobile app shall offer the ability to perform quick actions for efficiency; this will include the ability to expand the menu to perform all associated actions.
23. The mobile app shall have a home screen that can perform door, DSC actions and view video without having to change menus.
24. For Apple® and Android devices that allow thumbprint login, the mobile app shall allow login using this thumbprint. No extra information is required.
25. The mobile app shall support multiple SMS logins and servers stored in memory.
26. The SMS shall support gesture logins in order to login securely and quickly to the mobile app.
27. The mobile app shall be downloadable at no-charge from the App Store ® and Google Play ®.
28. The mobile app shall be supported but will not be limited to the following:
	1. Apple:
		1. iOS: 12.x
	2. Android:
		1. OS:
			1. Kitkat
			2. Lollipop
			3. Marshmallow
			4. Nougat
			5. Oreo

2.5.B Mobile app - EntraPass go Pass

1. EntraPass go Pass is an optional tool that will allow cardholders with this privilege to use their smartphone Apple® or Android® devices as their credentials.
2. EntraPass go Pass simulates a card swipe by sending the request over WI-FI or mobile data to the SMS Smartlink. The SMS sends the request to the controller; the controller devices then generate access or not to the door based on the real time door status.
	1. The SMS controller shall have the final say to unlock the door and the EntraPass go Pass request shall follow every rule of the door.
	2. EntraPass go Pass shall work on any Kantech controller.
	3. EntraPass go Pass shall not be tied to work on specific readers.
3. The EntraPass go Pass is paired to a SMS cardholder using encrypted one time use e-mail. The encrypted e-mail can only pair one smartphone at a time. A second smartphone trying to pair itself with the SMS cardholder shall be automatically rejected.
	1. The SMS operator can issue a new encrypted e-mail. Once completed the first smartphone is unpaired automatically and EntraPass go Pass stops working. The new smartphone can then be paired.
	2. The SMS operator can completely revoke the EntraPass go Pass credential if needed.
	3. The SMS operator shall use the SMS to customize the go Pass credential e-mail.
4. The EntraPass go Pass shall display all the doors assigned to the cardholder (using the access level).
	1. The doors shall be listed by site where the EntraPass go user shall be able to expand the list and see the doors within the site.
5. The first time an EntraPass go Pass user goes to the door, the EntraPass go Pass shall ask if they are onsite so the EntraPass go Pass can tag the location of the site.
6. Site lists shall be ordered by location distance and not alphabetical.
7. EntraPass go Pass shall be able to place their popular doors in the favorite window for quick access.
8. The concurrent connections are shared with the EntraPass web connections.
9. EntraPass go Pass shall support BLE geo fencing.
	1. When an ioSmart reader is wired over RS-485 to a KT-400 or KT-1 controller the reader shall emit a BLE signal. The door shall only be available to tap when the EntraPass go Pass is near the BLE signal of that reader.
	2. If the reader is not an ioSmart reader, the go Pass shall work without geo fencing for that reader.
10. EntraPass go pass shall support two-factor authentication
	1. When an ioSmart reader is configured in RS-485 mode the reader shall offer a multi-factor authentication to enter the door. Each door shall offer the following options but is not limited tothem:
		1. Two factor authentication not available; uses standard supported smart cards or prox cards.
		2. go Pass Biometric; to unlock the door, the cardholder uses the go Pass mobile app to tap the door and enter their biometric phone login. The reader still accepts smart cards.
		3. go Pass & disable card reader; to unlock the door, the cardholder uses the go Pass mobile app to tap the door and enter their biometric phone login. The reader does NOT accept any cards.

**2.6 INTEGRATION**

2.6.A SmartLink

1. The SmartLink application offers the ability to send messages to pagers and cell phones by e-mail. SmartLink provides instant e-mail notification of alarm events and the ability to e-mail reports.
2. Integration with other systems can also be done through the SmartLink API. This tool is used for advanced integration with third party applications like visitor management software, human resources systems, time and attendance systems, video systems, and HVAC.

2.6.B Card Gateway

1. The card gateway is an optional external interface that shall allow the client to make modifications to the system card database through an Oracle or MS-SQL database. The application can be installed and run on the server’s CPU. It shall allow for HR software integration and enable operators to modify, add, or obtain information on cards in real time.

**2.7 REDUNDANCY & MIRRORING**

2.7.A Redundancy Server

1. The SMS shall be able to support an optional Redundancy Server whose main function shall be to monitor the primary server and ensure automatic (hot standby) take over if necessary. The Redundancy Server shall have all the same characteristics and functions as the primary server.
2. The transition between these servers shall be completely transparent. When the primary server is operational once more, it shall be capable of synchronizing its database automatically with the Redundancy Server and then resume absolute control of the access management system. No human intervention shall be required in this operation.
3. The operator shall be able to perform any, and all operations during a fail-over synchronization between the primary server and Redundancy Server.
4. The SMS shall no longer allow the primary server to run and manage quick and custom event based reports. The quick and custom reports shall be managed by the active Redundancy Server. This will give power for the primary server to manage the database and the day-to-day operations.
5. The SMS shall allow the Redundancy Server to perform backups.
6. The SMS shall allow for asynchronous and synchronous Mirror Database of archives, time-attendance and video events. This allows for slower networks where the Redundancy Server is in a different building or city to only sync events at definable times (5, 15, 30, 60 minutes, 2 and 4 hours). The timer shall be configurable:
	1. In case of primary server failure the Redundancy Server shall start and take over. The database (data) is synchronized in real time at all times.
	2. Once the primary server restarts, the missing event shall be fully synchronized.
7. The system shall support the use of multiple simultaneous Redundancy Servers. The need to install third party (not EntraPass) licensing shall not be acceptable.
8. The SMS shall synchronize all Redundancy Servers and database instances at the same time and not in sequence

**2.8 SYBASE DATABASE ACCESS**

1. The SMS shall be able to support an optional remote Database Access server whose main function shall be to offer access in real time to the entire database. The operator shall have access to the entire database in read-only using third party protocols and tools. The operator shall have to be able to connect to the remote database by using industry standard tools such as but not limited to Crystal Reports ® and ODBC connections.
2. The SMS shall no longer allow the primary server to manage quick and custom event based reports. The quick and custom reports shall be managed by the active Database Access. This will give power to the primary server to manage the database and day-to-day operations.
3. The operator shall be able to create any customizable report using proper tools.
4. This option shall require activation in the SMS but shall not require an option code to purchase.
5. The SMS shall synchronize all Redundancy Servers and database instances at the same time and not in sequence

**2.9 HSPD-12 COMPLIANCE AND INTEGRATION**

1. The SMS shall be HSPD-12 compliant when integrating with PIVCheck Plus and Certificate Manager Solution.  The SMS and PIVCheck integration shall be seamless and the operator shall not need to enter the cardholder’s information twice.
2. The integration shall support up to three-factor authentication, extraction and verification of the cardholder’s data on the FIPS 201 smart card and shall perform a biometric match against the template stored on the card. Digital certificates shall verify against the issuer’s validation authority, SCVP or OCSP responders.  All cards shall be validated using the FIPS 201 challenge-response (CAK or PAK) in order to identify forged or cloned cards.  The SMS integration shall work with all PIV, TWIC, CAC and FRAC cards.
3. The PIVCheck solution shall verify the following items to ensure that the cardholder is the card owner, the card is authentic, and the card has not been revoked by the agency that issued it:
4. Smart card expiration date.
5. Non-duplicated card (forged/cloned).
6. Biometric
7. Certification status
8. PIN verification
9. The SMS shall natively support the FIPS 201 driver when using the KT-400 and KT-1 controllers and shall display the FIPS 201 card number correctly.
10. The SMS integration shall allow associating SMS card fields with the PIVCheck card field in order to have a seamless cardholder entry. The SMS integration shall allow but is not limited to be associated with the following fields:
11. User definable fields (ten).
12. Card holder pin
13. Card number
14. Card user name
15. Card type
16. Card status
17. The SMS integration with PIVCheck shall require option codes to activate all integration functions.

**2.10 OPERATION**

The SMS shall perform the following tasks:

1. Allow card access management for one or more buildings.
2. Control access to various doors equipped with a card reader. Allow the ability to set card use count options to limit the number of times a card can be used.
3. Ensure more secure control with the global anti-passback control function.
4. A command from a door controller may demand an immediate reaction from another door controller located at another site. This is a global functionality.
5. The SMS shall allow for operators to quickly search for a card holder within a Global Gateway or KT-NCC and locate them in the area.
6. The operator shall be able to transfer the searched cardholder to a different area.
7. The operators shall be able to transfer cards from one area to another quickly.
8. Allow automatic transfer of cards to an unknown area by a push of a button for emergency exit purposes.
9. Allow for a global mantrap using the synchronization of up to 255 groups of multiple doors and inputs within a Global Gateway or KT-NCC.
10. Monitor all defined alarm points as well as all doors controlled by card readers based on programmed schedules.
11. Manage the guard tour system.
12. Send transactions for which printing is required to one or more printers, based on a set schedule.
13. Access the system using the main and secondary menus (to which access is limited by a password) to make additions and required changes to various data files so that they can be updated by the user without the manufacturer’s assistance.
14. Enable the entry of access code data for every card or group of cards.
15. Seamlessly connect to onsite alarm systems.
16. Fully functional virtual keypad with DSC® PowerSeries PC1616, PC1832 and PC1864 alarm system in addition with the DSC Maxsys 4020 alarm panel. The operator shall perform all functions available on a standard keypad with the PowerSeries or MaxSys 4020 series alarm systems. The operator shall be able to use the computer keyboard or the mouse to perform actions on the virtual keypad.
17. Interface with the Simplex 4100ES Fire Panel thereby eliminating hardwired integration between the SMS controllers and the Simplex 4100ES fire panel to receive events from the Simplex 4100ES panel and view the virtual keypad.
18. Associate to each event a recording schedule for each destination (hard drive, monitor).
19. Automatically display all alarms on screen in text with optional graphic or picture and trigger a sound requiring an acknowledgement on the keyboard to stop the alarm.
20. Alarm pop-ups can be sent to many EntraPass Workstations. An alarm pop-up shall be acknowledged once by one operator.
21. Mandatory comments shall be added by the operator when acknowledging the alarm pop-up.
22. In the case of an unacknowledged alarm within a customizable time, the alarm shall be sent to all active operators with additional log information.
23. Each event should print on a log printer. For security reasons, each event shall be incremented with a print number. Numbering shall start from zero every day.
24. Generate reports and view them on the screen, output them to a printer, or send them to an e-mail address.
25. Supervise based on programmed schedules of specific points such as door contacts, volumetric detectors, mechanical points, high and low temperature sensors, or any other equipment necessary for good building management.
26. View and/or save video images.
27. When integrated into a DVR/NVR (American Dynamics, INTEVO, or Exacq), allow the management of the recordings of all the cameras using access system EntraPass Workstations.

1. When connected to a DVR/NVR (American Dynamics, INTEVO, or Exacq), allow the orientation of all PTZ cameras directly using the EntraPass Workstation mouse of the access system.
2. When connected to a DVR/NVR (American Dynamics, INTEVO, or Exacq), allow the recovery and storage of selected videos to an independent server.
3. The SMS shall offer the option to create four digit, five digit or six digit PIN for the cardholders.
4. The PIN length shall be defined SMS wide.
5. Save the database manually or automatically backup following a schedule.
6. Uninterrupted backups. The operator shall be able to perform any task during a SMS backup.
7. The operator shall be able to perform any and all operations during a fail-over synchronization between the primary server and Redundancy Server.
8. The SMS shall remind SMS operators via e-mail and messages (pop-ups) of the SMS KAP status. The SMS shall have pre-defined reminders set to:
9. Sixty days before KAP expiration.
10. Thirty days before KAP expiration.
11. Day of KAP expiration.
12. Thirty days after KAP expiration.
13. The SMS KAP reminder shall include, but not be limited to, SMS serial number tokens needed and SMS Edition.
14. The SMS shall offer administrators to post a message upon operator login. The message shall be customizable to be per operator and system wide.
15. The login message shall be configurable in both SMS languages, and appear on the SMS EntraPass Workstation, the mobile application (EntraPass go), and the SMS web application in the operator’s respective language.
16. The login message shall be configurable to specific timeframe (per operator):
	1. Never
	2. Always requires acknowledgement
	3. Only one acknowledgement
	4. Always requires acknowledgement until a specific date.
	5. Only one acknowledgement until a specific date.
17. The SMS administrator shall be able to force strong password rules. The SMS shall allow the SMS administrators to select the password settings. Password setting shall be configurable with the following rules:
	1. Password length between 8 and 20.
	2. Upper case characters between 0 and 20.
	3. Numeric characters between 0 and 20.
	4. Special characters between 0 and 20.
18. When the access control system manages parking lot entry and exit, it shall be possible to set a maximum number of vehicles authorized to access the parking area simultaneously. Once the parking lot is full, the system shall prevent access to any cardholder for as long as a parking space has not become available.
19. Allow the definition of a controller-based interlock function, that is, a cab or room delimited by two electronically controlled doors will not open simultaneously, creating a buffer between a low-security and a high-security area. The door leading to the high-security area will not open if the first door was locked until the person who is trying to access the high-security area meets all identity verification parameters. Allow for the definition of a Global Gateway or KT-NCC wide mantrap with interlocking groups (up to 255) of doors and inputs.
20. Allow for a dual custody option to add extra security to a door by requesting that two card holders must access the door together.
21. Save events on a hard drive according to required criteria.
22. The SMS shall allow storing the live transactions (events) portion of the system on a different local drive. This shall speed up performance of the SMS.
23. Once activated the SMS shall allow that the each door’s request-to-exit events shall be ignored and not stored.
	1. The events shall not be stored or viewed on the screen.
	2. Operators shall be able to ignore request-to-exit events on a per door basis by schedule.
24. It shall be possible to program on a KT-400 or KT-1 controllers’ reader to bypass a door contact on a schedule. The bypass shall be at the controller level and at the software level.
25. It shall be possible to bypass the door contact for door forced events, and door open too long events. It shall be possible to have the door open too long event be an optional bypass on a door basis.
26. Operators shall be able at any time to bypass the door contact manually from the SMS EntraPass Workstation.
27. It shall be possible to program a KT-400 or KT-1 controller reader a double and triple switch function.
28. It shall be possible to have the multi-swipe function activated on a predetermined schedule.
29. The double and triple swipes shall be able to be activated on a reader simultaneously each with their respective actions.
30. The multi-swipe function shall be able to but not limited to:
31. Toggle door unlock
32. Unlock door
33. Relock door
34. Temporarily unlock door
35. Activate Relay
36. Temporarily activate relay
37. Arm door partition request when using a Multi-Site Gateway.
38. Arm a virtual alarm panel request when using a Global Gateway or a KT-NCC.
39. Each cardholder shall have the option of having the multi-swipe function active.
40. A specific event shall be generated for any valid or invalid, double or triple swipes.
41. When using ioProx/ioSmart XSF/SSF format readers and the KT-400 controllers the SMS shall support eight readers for four doors.
42. Each door shall have two readers on the same reader port. The installation shall be simple and not require any extra modules to be added.
43. The exit reader of the door shall be wired on the same terminals as entry reader by simply by reversing D0/D1.
	* 1. The ioSmart readers shall communicate to the KT-400 over RS-485 on COM2 or standard Wiegand
44. Power, LED/piezo outputs shall be shared with the entry/exit reader.
45. The SMS shall offer specific exit reader functionalities but not limited to:
	* 1. Assigning a specific access level schedule to each reader independently.
		2. Enabling/disabling the entry/exit reader separately.
		3. Running reports on the readers separately or together.
		4. Follow the entry reader door name with a suffix of “-exit”.
		5. Share the same locking output.
		6. Share the same door contact.
		7. Share the same unlock schedule.
		8. Share the same unlock time and open time.
46. All eight readers shall be used if needed in a controller based anti-passback setup.
47. First person in shall unlock the door on a schedule:
48. With the KT-400 and the KT-1 a one hour grace period shall be configurable. The cardholder shall be able to enter within that grace period time and keep the door locked. When the door schedule activates, the door shall go on a schedule.
49. If no cardholder has presented their card within the grace period or within the schedule the door shall remain locked.
50. The “first person in” shall be configurable on a per door basis.
51. Perform the following operations from all EntraPass Workstations:
52. Lock or unlock, one time unlock, return to schedule one door or a group of doors.
53. View the last access event on the door.
54. Bypass the door contact and keep the door locked.
55. Temporarily unlock a door using a custom timer for additional door unlocking on KT-400 and KT-1 controller doors.
56. Disable and enable readers.
57. Activate or deactivate a relay or a group of relays.
58. View custom programmed comments in the component’s operation section.
59. Activate or deactivate the recording of one camera or a group of cameras.
60. Activate or deactivate a point or a group of points.
61. Program or modify one card or a group of cards.
62. Assign single door access exception to the card.
63. Validate or invalidate one card or a group of cards.
64. Change time and date.
65. Demand the system state in text or graphic mode.
66. Query, create and/or modify data on: access levels, schedules and holidays, access card, instructions, reports and log, doors, supervision points and relays, operator levels, and graphics.
67. Ability to use an easy to use system tree view to select the components.
68. View, which cards are in the roll call sectors.
69. View the card’s last known access in the roll call sector.
70. The operator shall be able to double click on components on the operation screen to automatically view the status in detailed text values
71. Each Global windows gateway application shall support a Global Gateway and a Multi-Site Gateway. One application per Global Gateway and Multi-Site Gateway shall be needed. The system shall support up to 40 Multi-Site Gateways.
72. Perform the following operations from the SmartLink task commander:
73. Lock, unlock toggle, return to schedule, temporary unlock, one time access arm and disarm any door.
74. Disable and enable any reader.
75. Lock, unlock, temporary unlock return to schedule, disable enable any elevator and elevator floor.
76. Activate, deactivate, temporary activate, toggle and return to schedule of any relay.
77. Shunt, unshunt, temporary shunt, toggle, return to schedule and continuous supervision of any input.
78. Arm, disarm and postpone any alarm system in a Global Gateway or KT-NCC.
79. Set count usage, manually overwrite the count, disable count usage, decrement count usage, and increment count usage for all the cards.
80. Send alarm e-mails.
81. The use of variables in the SmartLink task commander can be used instead of hard coded values.
82. Mass card modifications on without operator intervention.
83. Ability to use generically created commands to perform task on different components.
84. Each specific card shall have the ability to activate a specific component in the above mentioned states without the need to create hard coded the commands.
85. The SmartLink task commander shall process the commands on the first available SmartLink on the SMS.
86. The use of a specific SmartLink to run a specific SmartLink task commander shall not be accepted.
87. The SMS all allow for many SmartLinks to be installed without the need to purchase additional option codes.
88. The SmartLink task commander shall be run from any of the available SmartLink.
89. The SmartLink task commander shall allow for single or grouping of components of the same type to trigger the same task. The need to have a specific trigger programmed per component to trigger the same task shall not be accepted.

**2.11 EQUIPMENT**

2.11.Server, Database Access and Redundancy Server requirements

 The SMS server and Redundancy Server shall meet the following minimum requirements:

1. The server shall have a dual core processor or better.
	1. If doing video, the server shall have an Intel quad core processor or better.
2. The server shall have a 500 watt power unit.
3. The server shall have 4 GB RAM.
	1. If doing video, the server shall have an 8 GB of RAM or better.
4. The server shall have 100 GB hard disk drive space at minimum.
5. The server operating system shall be Windows Server 2008 R2, Windows Server 2012 R2, Windows Server 2016, Windows Server 2019, Windows 7, Windows 8.1, or Windows 10. All operating systems shall be 32-bit or 64-bit.
	1. The integration platform requirements shall possibly change the EntraPass requirements depending on integration products.
	2. Database Access shall support the following operating system: Windows Server 2008 R2, Windows Server 2012 R2, Windows Server 2016, Windows Server 2019, Windows 7, Windows 8.1, or Windows 10. All operating systems shall be 32-bit or 64-bit.
6. The server shall have a 100/1000 Base-T network adapter.
7. The server shall have a high quality multilingual keyboard.
8. The server shall have a two button ergonomic mouse.
9. The server shall have an on-off switch.
10. The server shall have an appropriate UPS.

2.11.B Global and Multi-Site Gateway, SmartLink and VideoVault, requirements

 The SMS Multi-Site Gateway shall meet the following minimum requirements:

1. The global or Multi-Site Gateway shall have a Dual core processor or better.
2. The global or Multi-Site Gateway shall have a 500 watt power unit.
3. The global or Multi-Site Gateway shall have 4 GB RAM.
4. The global or Multi-Site Gateway shall have 100 GB hard disk drive space.
5. The server operating system shall be Windows Server 2008 R2, Windows Server 2012 R2, Windows Server 2016, Windows Server 2019, Windows 7, Windows 8.1, or Windows 10. All operating systems shall be 32-bit or 64-bit.
	1. The integration platform requirements shall possibly change the EntraPass requirements depending on integration products.
6. The global or Multi-Site Gateway shall have a 100/1000 Base-T network adapter.
7. The global or Multi-Site Gateway shall have a high quality multilingual keyboard.
8. The global or Multi-Site Gateway shall have a two button ergonomic mouse.
9. The global or Multi-Site Gateway shall have an on-off switch.
10. The global or Multi-Site Gateway shall have an appropriate UPS.

2.11.C EntraPass Workstation requirements

 The SMS EntraPass Workstations shall meet the following minimum requirements:

1. The EntraPass Workstation shall have a dual core processor or better.
	1. If doing video, the EntraPass Workstation shall have an Intel quad core processor or better.
2. The EntraPass Workstation shall have a 500 watt power unit.
3. The EntraPass Workstation shall have 4 GB RAM.
	1. If doing video, the EntraPass Workstation shall have an 8 GB of RAM or better.
4. The EntraPass Workstation shall have 100 GB hard disk drive space.
5. The EntraPass Workstation shall have a 48 x CD-ROM drive.
6. The server operating system shall be Windows Server 2008 R2, Windows Server 2012 R2, Windows Server 2016, Windows Server 2019, Windows 7, Windows 8.1, or Windows 10. All operating systems shall be 32-bit or 64-bit.
	1. The integration platform requirements shall possibly change the EntraPass requirements depending on integration products
7. The EntraPass Workstation shall have a 100/1000 Base-T network adapter.
8. The EntraPass Workstation shall have a high quality multilingual keyboard.
9. The EntraPass Workstation shall have a two button ergonomic mouse.
10. The EntraPass Workstation shall have an on-off switch.
11. The EntraPass Workstation shall have an appropriate UPS.

2.11.D Controllers

 The SMS shall support the following door controllers:

1. Kantech KT-400:

The KT-400 is an Ethernet-ready four-door controller with sixteen monitored points, on-board door strike power, sixteen reader outputs, four relay outputs, and auxiliary power output. It shall accept Wiegand, proximity, ABA clock and data, bar code, magnetic, integrated keypad, and smart card reader types. It shall also support FIPS 201 cards, with and without checking the expiration date. It supports RS-232, RS-485 and 128-bit AES encrypted Ethernet 10/100 Base-T communication. It supports expansion modules to provide 256 inputs and 256 outputs. It shall support 256 double end of line inputs. It shall support up to eight card formats. The KT-400 shall support the following native features but will not be limited to them:

* + 1. Twenty intervals per schedule.
		2. Five access levels per card when connected to a Multi-Site Gateway.
		3. Thirteen access levels per card (12 of them with expiration dates) when connected to a Global Gateway.
		4. Multi-swipe capabilities
		5. 100,000 cards in standalone mode.
		6. 20,000 events in standalone mode.
		7. First person in with one hour grace period.
		8. Elevator unlock schedule per floor.
		9. Eight readers, four doors with ioProx XSF readers or ioSmart Readers.
		10. Eight Assa Abloy wireless locks (licenses required).
		11. ioSmart readers support communications over Wiegand or RS-485.
		12. ioModules input/output expansion module communicate over RS-485.
1. Kantech KT-1:

The KT-1 is an Ethernet-ready one-door controller PoE/PoE+ with four monitored points (single, double, or no end-of-line), on-board door strike power, two reader outputs, two relay outputs, and auxiliary power output. It shall support a lock output of 750mA when powered by 12dvc or PoE+. It shall accept Wiegand, proximity, ABA clock and data, bar code, magnetic, integrated keypad, and smart card reader types. It shall also support FIPS 201 cards, with and without checking the expiration date. It supports RS-232, RS-485 and 128-bit AES encrypted Ethernet 10/100Base-T communication. It shall support up to eight card formats. It supports expansion modules to provide 256 inputs and 256 outputs. It shall support 256 double end of line inputs.

* 1. The KT-1 shall support the following native features but will not be limited to them:
		1. Twenty intervals per schedule.
		2. Five access levels per card when connected to a Multi-Site Gateway.
		3. Thirteen access levels per card (12 of them with expiration dates) when connected to a Global Gateway.
		4. Multi-swipe capabilities
		5. 100,000 cards in standalone mode.
		6. 20,000 events in standalone mode.
		7. First person in with one hour grace period.
		8. Eight Assa Abloy wireless locks (licenses required).
		9. ioSmart readers support communications over Wiegand or RS-485.
		10. ioModules input/output expansion module communicate over RS-485.
	2. The multi-purpose single button shall be used for:
		1. Auto-enrolling a new KT-1 to the SMS over a local LAN segment.
		2. Enrolling a new KT-1 to a primary KT-1 over IP (over local LAN segment).
		3. Status of the controller’s communication, locks, and relays.
		4. Used as a request-to-exit.
	3. The multi-purpose button shall be LED configurable.
	4. The KT-1 shall be installed in two ways:
		1. Mountable quickly and efficiently on a single gang installation on the secure side of the door.
		2. In a cabinet for on a PCB board. This configuration shall be support DSC integration.

1. Kantech KT-300:

The KT-300 is a two-door controller with eight monitored points on board expandable to sixteen, door strike power, auxiliary power output, and two auxiliary outputs. It shall accept Wiegand, proximity, bar code, magnetic and integrated keypad reader types. It supports RS-232, RS-485, and Combus communication. It supports relay, input, and output expansion modules. The KT-300 is available in 128k and 512k memory versions.

1. Kantech KT-100:

The KT-100 is a one-door controller with four monitored points, door strike power, and four auxiliary outputs. It shall accept Wiegand, proximity, bar code, magnetic and integrated keypad reader types. It supports RS-485 communication.

1. Kantech KT-200 (Legacy).

 2.11.E Kantech Telephone Entry System (KTES)

1. The KTES enables tenants to grant access to the building, to their visitors, using their own telephone line or cellular telephone. The KTES supports 250 tenants with the option of supporting up to 3,000 tenants. The KTES also includes:
* Four lines x 20 characters LCD module with controllable LED backlighting.
* Programming menus available in three languages (English, French and Spanish).
* Built-in RS-485
* 128-bit AES encrypted Ethernet.
* Internal modem
* Three relays
* Microphone
* Speaker
* Backup battery
1. Optional KTES accessories are:
* Heater kit
* Postal lock
* Color camera
* Goose neck mounting
* Paper index (flush mounted).
1. The KTES shall be programmed using the keypad and LCD for standalone mode or using the SMS.
2. The unit shall support a Wiegand reader that will allow tenants to wipe their cards and enter the building.
3. The KTES shall employ flashable firmware with auto update.

 2.11.F Network Communications Controller (KT-NCC)

1. The KT-NCC shall replace a Global Gateway and remove a layer of PC’s. It shall acquire all information from all input channels and relay the results back to all output channels through the controller loops. The KT-NCC shall communicate with the server through an Ethernet 10/100 Base-T port. It shall connect up to seven loops per gateway and shall feature four relays. The KT-NCC shall support up to 128 controllers and 256 doors.
2. The KT-NCC shall employ flashable firmware with auto update. There shall be embedded redundancy to protect critical data.

2.11.G Card and Reader Support

1. The SMS shall support configuration of unlimited card formats.
2. The SMS shall support up to two card formats per KT-100 and KT-300 controller.
3. The SMS shall support up to eight card formats per KT-400 or KT-1 controller.
4. The SMS shall support readers that provide Wiegand signaling and magnetic ABA signaling to include:
	1. Kantech ioProx family of readers.
	2. Kantech ioSmart family of readers.
	3. Wiegand swipe readers
	4. Proximity readers
	5. Biometric readers
	6. Smart card readers
	7. Wireless readers
	8. Magnetic readers

**PART III EXECUTION**

**3.1 TESTING**

* 1. The software shall be entered into the SMS computer systems and debugged. The contractor shall be responsible for documenting and entering the initial database into the system. The contractor shall provide the necessary blank forms with instructions to fill‑in all the required data information that will make up the database. The database shall then be reviewed by the contractor and entered into the system. Prior to full operation, a complete demonstration of the computer real‑time functions shall be performed. A printed validation log shall be provided as proof of operation for each software application package. In addition, a point utilization report shall be furnished listing each point, the associated programs utilizing that point as an input or output, and the programs which that point initiates.
	2. Upon satisfactory on‑line operation of the system software, the entire installation including all subsystems shall be inspected. The contractor shall perform all tests, furnish all test equipment and consumable supplies necessary and perform any work as required to establish performance levels for the system in accordance with the specifications. Each device shall be tested as a working component of the completed system. All system controls shall be inspected for proper operation and response.
	3. Tests shall demonstrate the response time and display format of each different type of input sensor and output control device. Response time shall be measured with the system functioning at full capacity. Computer operation shall be tested with the complete data file.
	4. The contractor shall maintain a complete log of all inspections and tests. Upon final completion of system tests, a copy of the log records shall be submitted as part of the as-built documentation.

**3.2 TRAINING**

The contractor shall provide a competent trainer who has extensive experience on the installed systems and in delivering training to provide the instruction. As an alternate, the contractor may propose the use of factory training personnel and coordinate the number of personnel to be trained.

**3.3 MAINTENANCE**

1. The contractor shall offer a Kantech Advantage Program (KAP) to provide twelve additional months of free software updates and online training for the end user.
2. Technical support is available at no charge to all Kantech dealers whether or not they have a KAP activated for the systems they are supporting.

END OF SPECIFICATIONS

